## 2000
TOWER POWER LTD GENERATIONS FOR YEAR 2000
TONGA POWER: TONGATAPU 2000 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | January: 0; December: 2938433 | 2938433
Power retained by licence | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38065 | 38065
Power supplied to customers | kWh | January: 0; December: 2900368 | 2900368
Billing | kWh | January: 0; December: 0 | 0
Transmission losses | kWh | January: 0; December: 0 | 0
Distribution losses | kWh | January: 0; December: 0 | 0
Unmetered read | kWh | January: 0; December: 0 | 0
Installed capacity | kW | January: 0; December: 0 | 0
Derated capacity | kW | January: 0; December: 0 | 0
Fuel consumed in generation | litre | January: 0; December: 741342.43 | 741342.43
Lubricating oil used | litre | January: 0; December: 2696
Number of consumer | number | January: 0; December: 0 | 0
Station running time to generate | hr | January: 0; December: 0 | 0
Peak demand | kW | January: 0; December: 0 | 0
Minimum demand | kW | January: 0; December: 0 | 0
Fuel rate | kWh/ltr | January: 0; December: 3.96 | 3.96
TONGA POWER: VAVA'U 2000 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | [12 empty] | 0
Power retained by licence | kWh | [12 empty] | 0
Power supplied to customers | kWh | [12 empty] | 0
Billing | kWh | [12 empty] | 0
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | [12 empty] | 0
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | [12 empty] | 0
Derated capacity | kW | [12 empty] | 0
Fuel consumed in generation | litre | [12 empty] | 0
Lubricating oil used | litre | [12 empty] | 0
Number of consumer | number | [12 empty] | 0
Station running time to generate | hr | [12 empty] | 0
Peak demand | kW | [12 empty] | 0
Minimum demand | kW | [12 empty] | 0
Fuel rate | kWh/ltr | [12 empty] | 0
TONGA POWER: HA'APAI 2000 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | [12 empty] | 0
Power retained by licence | kWh | [12 empty] | 0
Power supplied to customers | kWh | [12 empty] | 0
Billing | kWh | [12 empty] | 0
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | [12 empty] | 0
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | [12 empty] | 0
Derated capacity | kW | [12 empty] | 0
Fuel consumed in generation | litre | [12 empty] | 0
Lubricating oil used | litre | [12 empty] | 0
Number of consumer | number | [12 empty] | 0
Station running time to generate | hr | [12 empty] | 0
Peak demand | kW | [12 empty] | 0
Minimum demand | kW | [12 empty] | 0
Fuel rate | kWh/ltr | [12 empty] | 0
TONGA POWER: 'EUA 2000 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | [12 empty] | 0
Power retained by licence | kWh | [12 empty] | 0
Power supplied to customers | kWh | [12 empty] | 0
Billing | kWh | [12 empty] | 0
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | [12 empty] | 0
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | [12 empty] | 0
Derated capacity | kW | [12 empty] | 0
Fuel consumed in generation | litre | [12 empty] | 0
Lubricating oil used | litre | [12 empty] | 0
Number of consumer | number | [12 empty] | 0
Station running time to generate | hr | [12 empty] | 0
Peak demand | kW | [12 empty] | 0
Minimum demand | kW | [12 empty] | 0
Fuel rate | kWh/ltr | [12 empty] | 0
TONGA POWER: TONGA 2000 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2938433 | 2938433
Power retained by licence | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38065 | 38065
Power supplied to customers | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2900368 | 2900368
Billing | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transmission losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unmetered read | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installed capacity | kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derated capacity | kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fuel consumed in generation | litre | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741342.43 | 741342.43
Lubricating oil used | litre | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2696 | 2696
Number of consumer | number | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Station running time to generate | hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak demand | kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum demand | kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fuel rate | kWh/ltr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.96 | 3.96

## 2001
TOWER POWER LTD GENERATIONS FOR YEAR 2001
|  | 0.66695 | 0.73541 | 0.73533 | 0.7458 | 0.71041 | 0.59085 | 0.76665 | 0.71725 | 0.98299 | 0.72279 | 0.79 | 0.84821
TONGA POWER: TONGATAPU 2001 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 3084020 | 2812510 | 2934534 | 2784009 | 2896724 | 2656349 | 2670477 | 2726924 | 2621748 | 2744755 | 2826764 | 2983313 | 33742127
Power retained by licence | kWh | 40908 | 36598 | 40642 | 38939 | 41074 | 43489 | 37565 | 45372 | 44820 | 40119 | 46480 | 47665 | 503671
Power supplied to customers | kWh | 3043112 | 2775912 | 2893892 | 2745070 | 2855650 | 2612860 | 2632912 | 2681552 | 2576928 | 2704636 | 2780284 | 2935648 | 33238456
Billing | kWh | 2029605.6382 | 2041441.9608 | 2127952.9567 | 2047271.5296 | 2028692.1887 | 1543813.1422 | 2018515.5277 | 1923347.1095 | 2533106.2547 | 1954891.05 | 2196424.36 | 2490034.5635 | 24935096.2815
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 1013506.3618 | 734470.0392 | 765939.0433 | 697798.4704 | 826957.8113 | 1069046.8578 | 614396.4723 | 758204.8905 | 43821.7453 | 749744.95 | 583859.64 | 445613.4365 | 8303359.7185
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400
Derated capacity | kW | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000
Fuel consumed in generation | litre | 771466.34 | 708454.7 | 739471.02 | 705562.59 | 732548.19 | 667998.92 | 670275.15 | 682285.72 | 657841.61 | 675285.17 | 724135.21 | 749558 | 8484882.62
Lubricating oil used | litre | 3176 | 941 | 2530 | 1678 | 2485 | 1060 | 3949 | 1710 | 1690 | 1735 | 2591 | 1929 | 25474
Number of consumer | number | 14364.5461 | 14359.9412 | 14363.0898 | 14368.4217 | 14371.378 | 14372.1375 | 14352.3083 | 14332.3119 | 14381.9816 | 14400.4128 | 14389.1157 | 14376.6944 | 14400.4128
Station running time to generate | hr | 2663 | 2431 | 2132 | 2024 | 2261 | 2491 | 2403 | 2217 | 2216 | 2516 | 2168 | 2074 | 27596
Peak demand | kW | 5875 | 6000 | 5680 | 5830 | 5955 | 5707 | 5702 | 5713 | 5697 | 5746 | 6045 | 6053 | 6053
Minimum demand | kW | 2938 | 2146 | 2219 | 2240 | 2585 | 1900 | 2373 | 2355 | 1339 | 2442 | 2478 | 1529 | 1339
Fuel rate | kWh/ltr | 4 | 3.97 | 3.97 | 3.95 | 3.95 | 3.98 | 3.98 | 4 | 3.99 | 4.06 | 3.9 | 3.98 | 47.73
TONGA POWER: VAVA'U 2001 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 303538.9712 | 304325.6097 | 303006.1745 | 304330.0269 | 305594.2355 | 307029.2832 | 296948.4976 | 309045.4403 | 295089.5638 | 312273.1413 | 313179.4872 | 315639.5688 | 3670000
Power retained by licence | kWh | 13494.3509 | 13508.1834 | 13545.8535 | 13527.4107 | 13395.9557 | 13563.5137 | 13696.534 | 13453.6396 | 12870.1355 | 14233.7457 | 14228.6151 | 12482.0621 | 162000
Power supplied to customers | kWh | 290044.6204 | 290817.4263 | 289460.321 | 290802.6162 | 292198.2798 | 293465.7695 | 283251.9636 | 295591.8006 | 282219.4283 | 298039.3956 | 298950.872 | 303157.5067 | 3508000
Billing | kWh | 216528.4333 | 269147.3948 | 197072.1287 | 283180.4835 | 208737.3623 | 173277.1854 | 237956.5143 | 242917.0414 | 259983.6219 | 230624.0644 | 263076.7674 | 298105.8156 | 2880606.8131
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 73516.187 | 21670.0314 | 92388.1923 | 7622.1327 | 83460.9175 | 120188.584 | 45295.4493 | 52674.7592 | 22235.8063 | 67415.3312 | 35874.1046 | 5051.6911 | 627393.1869 | 700 | 58.3333
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158
Derated capacity | kW | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1
Fuel consumed in generation | litre | 88991.0036 | 88987.3063 | 89022.679 | 89007.6912 | 88946.3378 | 88972.5172 | 89164.1698 | 88947.7398 | 88700.9245 | 89077.2346 | 89930.7804 | 88082.0198 | 1067830.4041
Lubricating oil used | litre | 266.973 | 266.9619 | 267.068 | 267.0231 | 266.839 | 266.9176 | 267.4925 | 266.8432 | 266.1028 | 267.2317 | 269.7923 | 264.2461 | 3203.4912
Number of consumer | number | 3192.9285 | 3192.9286 | 3192.9287 | 3192.9286 | 3192.9284 | 3192.9283 | 3192.9287 | 3192.9291 | 3192.929 | 3192.9281 | 3192.9271 | 3192.9279 | 3192.9291
Station running time to generate | hr | [12 empty] | 0
Peak demand | kW | 861.9099 | 861.8883 | 861.9 | 861.8648 | 861.96 | 862.0524 | 861.7941 | 861.7582 | 861.9704 | 861.6538 | 862.5313 | 862.6067 | 862.6067
Minimum demand | kW | [12 empty] | 0
Fuel rate | kWh/ltr | [12 empty] | 0
TONGA POWER: HA'APAI 2001 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 93156.4743 | 93136.2602 | 92903.3688 | 92707.2413 | 92574.5401 | 92723.8915 | 94893.5437 | 93014.9757 | 91506.0204 | 91530.4762 | 91778.3333 | 93620 | 1113545.1255
Power retained by licence | kWh | 2395.7128 | 2399.674 | 2406.0851 | 2379.6136 | 2380.8987 | 2342.3434 | 2465.6617 | 2423.4415 | 2444.5516 | 2220.7844 | 2388.6098 | 2111.0117 | 28358.3883
Power supplied to customers | kWh | 90760.7615 | 90736.5862 | 90497.2837 | 90327.6277 | 90193.6414 | 90381.5481 | 92427.8819 | 90591.5342 | 89061.4688 | 89309.6918 | 89389.7235 | 91508.9883 | 1085186.7372
Billing | kWh | 52297.0542 | 54901.3543 | 59888.5871 | 61235.4428 | 61009.8326 | 61952.7484 | 67956.1201 | 55366.8024 | 56276.6869 | 61427.9925 | 66313.9935 | 72470.1387 | 731096.7536
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 38463.7073 | 35835.2318 | 30608.6966 | 29092.185 | 29183.8088 | 28428.7997 | 24471.7618 | 35224.7318 | 32784.7819 | 27881.6993 | 23075.7301 | 19038.8495 | 354089.9836 | 125.2857 | 10.4405
Unmetered read | kWh | [12 empty] | 0 | 113.1429 | 9.4286
Installed capacity | kW | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 130.4857 | 10.8738
Derated capacity | kW | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 128.9829 | 10.7486
Fuel consumed in generation | litre | 28714.5456 | 28707.3416 | 28639.1235 | 28586.7566 | 28565.839 | 28625.5763 | 29162.6368 | 28664.1173 | 28229.8148 | 28272.5556 | 28440.3333 | 28984 | 343592.6405 | 127.1794 | 10.5983
Lubricating oil used | litre | 66.0912 | 64.6057 | 58.6812 | 58.0095 | 60.7386 | 68.8307 | 85.6814 | 55.6929 | 23.134 | 53.9793 | 77.1132 | 117.3835 | 789.941 | 125.0153 | 10.4179
Number of consumer | number | 984.1588 | 984.1588 | 984.1588 | 984.1586 | 984.1585 | 984.1588 | 984.1591 | 984.1591 | 984.1585 | 984.1576 | 984.1577 | 984.1606 | 984.1606 | 124.9612 | 10.4134
Station running time to generate | hr | [12 empty] | 0 | 127.3249 | 10.6104
Peak demand | kW | 238.7813 | 238.7018 | 238.7515 | 238.9156 | 238.5277 | 238.1951 | 239.5958 | 238.225 | 239.05 | 239.9 | 236.2 | 236.2 | 239.9 | 126.6927 | 10.5577
Minimum demand | kW | [12 empty] | 0 | 126.2347 | 10.5196
Fuel rate | kWh/ltr | 3.2442 | 3.2443 | 3.2439 | 3.243 | 3.2407 | 3.2392 | 3.2539 | 3.245 | 3.2415 | 3.2374 | 3.227 | 3.2301 | 38.8904
TONGA POWER: 'EUA 2001 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 71957.0693 | 72047.3958 | 72747.7377 | 72889.4278 | 74044.7962 | 65642.7694 | 71491.7813 | 74835.5769 | 72679.681 | 77650.1311 | 73881.2589 | 82132.3745 | 882000
Power retained by licence | kWh | 2773.8553 | 2777.3373 | 2804.3346 | 2809.7965 | 2854.3345 | 2530.4469 | 2755.919 | 2884.8182 | 2801.7111 | 2993.3157 | 2848.0304 | 3166.1006 | 34000
Power supplied to customers | kWh | 69183.214 | 69270.0585 | 69943.4031 | 70079.6313 | 71190.4616 | 63112.3225 | 68735.8623 | 71950.7588 | 69877.97 | 74656.8154 | 71033.2285 | 78966.2739 | 848000
Billing | kWh | 50352.9623 | 51259.8433 | 52457.5523 | 54662.1124 | 51277.1181 | 52476.2489 | 57008.4718 | 63080.6738 | 62639.4365 | 55609.9954 | 63619.1824 | 78064.4387 | 692508.036
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 18830.2517 | 18010.2152 | 17485.8508 | 15417.5189 | 19913.3436 | 10636.0736 | 11727.3905 | 8870.085 | 7238.5334 | 19046.82 | 7414.0461 | 901.8351 | 155491.964 | 70.8 | 6 | 5.9 | 0.5
Unmetered read | kWh | [12 empty] | 0 | 67.76 | 6.2
Installed capacity | kW | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 64.112 | 6.44
Derated capacity | kW | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 59.7344 | 6.728
Fuel consumed in generation | litre | 22332.5409 | 22406.5931 | 22371.1402 | 22343.599 | 22290.9363 | 22291.4883 | 22291.4883 | 22850.9069 | 22158.4224 | 22178.352 | 21974.96 | 22294.8 | 267785.2273 | 54.4813 | 7.0736
Lubricating oil used | litre | 147.4019 | 147.4965 | 140.6004 | 153.1154 | 143.5973 | 152.7287 | 144.7785 | 114.0407 | 228.7428 | 97.5617 | 198.171 | 108.2362 | 1776.471 | 63.3775 | 6.4883
Number of consumer | number | 1045.0081 | 1045.0083 | 1045.008 | 1045.0074 | 1045.007 | 1045.0083 | 1045.0097 | 1045.0092 | 1045.0065 | 1045.0035 | 1045.0046 | 1045.0165 | 1045.0165 | 61.893 | 6.586
Station running time to generate | hr | [12 empty] | 0 | 60.7197 | 6.6632
Peak demand | kW | 224.2303 | 224.2111 | 223.9069 | 223.7057 | 223.5385 | 223.2413 | 226.7783 | 224.0956 | 222.082 | 222.4988 | 222.5347 | 221.4583 | 226.7783 | 60.0412 | 6.7078
Minimum demand | kW | [12 empty] | 0 | 60.1025 | 6.7038
Fuel rate | kWh/ltr | [12 empty] | 0
TONGA POWER: TONGA 2001 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 3552672.5148 | 3282019.2656 | 3403191.281 | 3253935.6961 | 3368937.5719 | 3121744.9441 | 3133810.8226 | 3203819.9929 | 3081023.2652 | 3226208.7487 | 3305603.0794 | 3474704.9433 | 39407672.1255
Power retained by licence | kWh | 59571.9189 | 55283.1947 | 59398.2732 | 57655.8208 | 59705.189 | 61925.304 | 56483.1147 | 64133.8993 | 62936.3982 | 59566.8458 | 65945.2553 | 65424.1744 | 728029.3883
Power supplied to customers | kWh | 3493100.5959 | 3226736.071 | 3343793.0078 | 3196279.8752 | 3309232.3829 | 3059819.6401 | 3077327.7079 | 3139686.0936 | 3018086.867 | 3166641.9029 | 3239657.8241 | 3409280.7688 | 38679642.7372
Billing | kWh | 2348784.0881 | 2416750.5533 | 2437371.2248 | 2446349.5683 | 2349716.5017 | 1831519.325 | 2381436.634 | 2284711.6271 | 2912006 | 2302553.1023 | 2589434.3033 | 2938674.9566 | 29239307.8843
Transmission losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution losses | kWh | 1144316.5079 | 809985.5177 | 906421.783 | 749930.307 | 959515.8812 | 1228300.315 | 695891.0739 | 854974.4666 | 106080.8671 | 864088.8006 | 650223.5209 | 470605.8122 | 9440334.853
Unmetered read | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installed capacity | kW | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117
Derated capacity | kW | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5
Fuel consumed in generation | litre | 911504.4301 | 848555.941 | 879503.9627 | 845500.6368 | 872351.3032 | 807888.5018 | 810893.4449 | 822748.484 | 796930.7717 | 814813.3122 | 864481.2837 | 888918.8198 | 10164090.8918
Lubricating oil used | litre | 3656.4661 | 1420.0641 | 2996.3496 | 2156.1479 | 2956.1749 | 1548.4769 | 4446.9524 | 2146.5768 | 2207.9796 | 2153.7726 | 3136.0766 | 2418.8658 | 31243.9033
Number of consumer | number | 19586.6415 | 19582.0369 | 19585.1853 | 19590.5163 | 19593.4718 | 19594.2329 | 19574.4058 | 19554.4093 | 19604.0756 | 19622.5021 | 19611.2052 | 19598.7994 | 19622.519
Station running time to generate | hr | 2663 | 2431 | 2132 | 2024 | 2261 | 2491 | 2403 | 2217 | 2216 | 2516 | 2168 | 2074 | 27596
Peak demand | kW | 7199.9215 | 7324.8011 | 7004.5584 | 7154.4862 | 7279.0262 | 7030.4889 | 7030.1682 | 7037.0789 | 7020.1023 | 7070.0526 | 7366.2661 | 7373.265 | 7373.265
Minimum demand | kW | 2938 | 2146 | 2219 | 2240 | 2585 | 1900 | 2373 | 2355 | 1339 | 2442 | 2478 | 1529 | 1339
Fuel rate | kWh/ltr | 3.8976 | 3.8678 | 3.8694 | 3.8485 | 3.8619 | 3.8641 | 3.8646 | 3.894 | 3.8661 | 3.9594 | 3.8238 | 3.9089 | 3.8771

## 2002
TOWER POWER LTD GENERATIONS FOR YEAR 2002
|  | 0.66695 | 0.73541 | 0.73533 | 0.7458 | 0.71041 | 0.59085 | 0.76665 | 0.71725 | 0.98299 | 0.72279 | 0.79 | 0.84821
TONGA POWER: TONGATAPU 2002 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 3187298 | 2868815 | 3305008 | 3112118 | 3189747 | 3019432 | 3092351 | 2961189 | 2912427 | 3062551 | 3057091 | 3319135 | 37087162
Power retained by licence | kWh | 40662 | 38523 | 46610 | 43734 | 40263 | 46316 | 49587 | 49341 | 46219 | 40119 | 40455 | 42179 | 524008
Power supplied to customers | kWh | 3146636 | 2830292 | 3258398 | 3068384 | 3149484 | 2973116 | 3042764 | 2911848 | 2866208 | 3022432 | 3016636 | 3276956 | 36563154
Billing | kWh | 2098651.0411 | 2081433.7234 | 2395983.5606 | 2288398.9134 | 2237435.8164 | 1756671.0632 | 2332727.5584 | 2088527.2536 | 2817466.9265 | 2184591.6663 | 2383142.44 | 2779534.0937 | 27444564.0566
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 1047984.9589 | 748858.2766 | 862414.4394 | 779985.0866 | 912048.1836 | 1216444.9368 | 710036.4416 | 823320.7464 | 48741.0735 | 837840.3337 | 633493.56 | 497421.9063 | 9118589.9434
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400
Derated capacity | kW | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000
Fuel consumed in generation | litre | 808242.75 | 732051.64 | 847933.91 | 789239.89 | 800182.61 | 750981.84 | 776992 | 748186 | 738446 | 765720 | 763972 | 838567 | 9360515.64
Lubricating oil used | litre | 2468 | 2578 | 2020 | 2761 | 2227 | 1880 | 2719 | 2503 | 2886 | 2636 | 1260 | 2592 | 28530
Number of consumer | number | 14352.3083 | 14332.3119 | 14381.9816 | 14400.4128 | 14389.1157 | 14376.6944 | 14233.3333 | 14212.3333 | 14680 | 14511 | 14321.3333 | 14302.1667 | 14680
Station running time to generate | hr | 1277 | 1904 | 2108 | 2032 | 2011 | 1961 | 1972 | 2311 | 1957 | 2141 | 2012 | 2046 | 23732
Peak demand | kW | 6078 | 6244 | 6477 | 6473 | 6434 | 6409 | 6462 | 6188 | 6356 | 6662 | 6470 | 6791 | 6791
Minimum demand | kW | 3043 | 1913 | 3090 | 2018 | 2655 | 2995 | 2750 | 2766 | 2769 | 2701 | 2854 | 3112 | 1913
Fuel rate | kWh/ltr | 3.9435 | 3.9189 | 3.8977 | 3.9432 | 3.9863 | 4.0206 | 3.9799 | 3.9578 | 3.944 | 3.9996 | 4.0016 | 3.9581 | 3.9621
|  | 0.74653 | 0.92549 | 0.68083 | 0.97379 | 0.71437 | 0.59045 | 0.84009 | 0.8218 | 0.92121 | 0.7738 | 0.88 | 0.98334
TONGA POWER: VAVA'U 2001 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 328206.0481 | 329056.6127 | 327629.9537 | 329061.3889 | 330428.3333 | 331980 | 321080 | 334160 | 319070 | 337650 | 338630 | 341290 | 3968242.3367
Power retained by licence | kWh | 17381.26 | 17383.5512 | 17394.5288 | 17378.1334 | 17368.8267 | 17392.7159 | 0 | 17312.5515 | 17331.6 | 17488.2727 | 17621.3333 | 16809 | 190861.7737
Power supplied to customers | kWh | 310824.7881 | 311673.0614 | 310235.4249 | 311683.2555 | 313059.5066 | 314587.2841 | 321080 | 316847.4485 | 301738.4 | 320161.7273 | 321008.6667 | 324481 | 3777380.563
Billing | kWh | 232041.5539 | 288448.9888 | 211216.3607 | 303513.8272 | 223639.9738 | 185748.4069 | 269735.3855 | 260384.9112 | 277964.712 | 247742.4122 | 282487.6267 | 319073.983 | 3101998.142
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 78783.2342 | 23224.0727 | 99019.0641 | 8169.4284 | 89419.5328 | 128838.8772 | 51344.6145 | 56462.5373 | 23773.688 | 72419.315 | 38521.04 | 5407.017 | 675382.4211
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158
Derated capacity | kW | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1
Fuel consumed in generation | litre | 96222.8523 | 96218.8546 | 96257.1018 | 96240.896 | 96174.5568 | 96202.8636 | 96410.0909 | 96176.0727 | 95909.2 | 96316.0909 | 97239 | 95240 | 1154607.5798
Lubricating oil used | litre | 303.838 | 303.7878 | 303.9877 | 303.7384 | 303.6373 | 304.5874 | 302.9906 | 303.3338 | 307.4379 | 298.2 | 304.3636 | 319.75 | 3659.6526
Number of consumer | number | 3192.9287 | 3192.9291 | 3192.929 | 3192.9281 | 3192.9271 | 3192.9279 | 3192.9308 | 3192.9318 | 3192.9282 | 3192.9227 | 3192.9214 | 3192.9323 | 3192.9323
Station running time to generate | hr | [12 empty] | 0
Peak demand | kW | 861.8098 | 861.7891 | 861.8616 | 861.7785 | 861.7273 | 862.0791 | 861.5291 | 861.5738 | 863.1343 | 859.879 | 861.7082 | 867.8158 | 867.8158
Minimum demand | kW | 367.7661 | 367.7522 | 367.7801 | 367.766 | 367.7104 | 367.864 | 367.7237 | 367.5434 | 368.3248 | 367.3029 | 367.0026 | 370.6691 | 367.0026
Fuel rate | kWh/ltr | 3.4109 | 3.4199 | 3.4037 | 3.4191 | 3.4357 | 3.4508 | 3.3304 | 3.4745 | 3.3268 | 3.5056 | 3.4825 | 3.5835 | 3.4369
|  | 0.85437 | 1.0064 | 0.95065 | 0.85306 | 0.86012 | 1.0705 | 1.0163 | 0.73484 | 0.80832 | 0.79715 | 1.0216 | 1.0255
TONGA POWER: HA'APAI 2002 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 92801.6089 | 91521.4077 | 91613.7318 | 92113.2653 | 94122.8571 | 97140 | 102850 | 80250 | 82560 | 92260 | 95610 | 108190 | 1121032.8708
Power retained by licence | kWh | 1528.0892 | 1659.0802 | 1837.5056 | 1287.25 | 1029.8 | 858.1667 | 805.8333 | 1707 | 2274.5 | 2293.6667 | 2838 | 3443.3333 | 21562.225
Power supplied to customers | kWh | 91273.5197 | 89862.3275 | 89776.2262 | 90826.0153 | 93093.0571 | 96281.8333 | 102044.1667 | 78543 | 80285.5 | 89966.3333 | 92772 | 104746.6667 | 1099470.6459
Billing | kWh | 61896.5357 | 64900.6797 | 70660.8454 | 72660.8122 | 72568.8581 | 73742.5044 | 80956.3027 | 65555.408 | 66158.1137 | 71931.9729 | 77354.1654 | 83797.3333 | 862183.5317
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 29376.9839 | 24961.6478 | 19115.3808 | 18165.2031 | 20524.199 | 22539.3289 | 21087.864 | 12987.592 | 14127.3863 | 18034.3605 | 15417.8346 | 20949.3333 | 237287.1142
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
Derated capacity | kW | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4
Fuel consumed in generation | litre | 29162.6368 | 28664.1173 | 28229.8148 | 28272.5556 | 28440.3333 | 28984 | 32385 | 25673 | 25624 | 28529 | 29447 | 32246 | 345657.4578
Lubricating oil used | litre | 77.136 | 75.4023 | 68.4877 | 67.7037 | 70.8889 | 80.3333 | 100 | 65 | 27 | 63 | 90 | 137 | 921.9518
Number of consumer | number | 984.1591 | 984.1591 | 984.1585 | 984.1576 | 984.1577 | 984.1606 | 984.1613 | 984.159 | 984.1546 | 984.1525 | 984.1583 | 984.1781 | 984.1781
Station running time to generate | hr | 2030 | 2000.3333 | 2078.75 | 2052.7708 | 2052.7708 | 2053.5595 | 1915.5387 | 2105.2054 | 2096.6667 | 2042.8439 | 2042.8439 | 2717 | 25188.2831
Peak demand | kW | 239.5958 | 238.225 | 239.05 | 239.9 | 236.2 | 236.2 | 248 | 230 | 244 | 245 | 214 | 236.2 | 248
Minimum demand | kW | 75.6458 | 74.125 | 74.25 | 75.5 | 73 | 73 | 84 | 65 | 75 | 83 | 58 | 73 | 58
Fuel rate | kWh/ltr | 3.1822 | 3.1929 | 3.2453 | 3.258 | 3.3095 | 3.3515 | 3.1759 | 3.1259 | 3.222 | 3.2339 | 3.2469 | 3.3551 | 3.2432
|  | 0.72782 | 0.74 | 0.75 | 0.78 | 0.72028 | 0.83147 | 0.82938 | 0.87672 | 0.89641 | 0.74487 | 0.89563 | 0.98858
TONGA POWER: 'Eua 2002 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 68389.2176 | 68475.0654 | 69140.6822 | 69275.3469 | 70373.4286 | 62388 | 67947 | 71125 | 69076 | 73800 | 70218 | 78060 | 838267.7407
Power retained by licence | kWh | 673.6481 | 573.3333 | 637.8889 | 692.6667 | 849.3333 | 0 | 957 | 905 | 36 | 1080 | 1178 | 940 | 8522.8704
Power supplied to customers | kWh | 67715.5694 | 67901.7321 | 68502.7933 | 68582.6803 | 69524.0952 | 62388 | 66990 | 70220 | 69040 | 72720 | 69040 | 77120 | 829744.8703
Billing | kWh | 49284.7805 | 50247.2817 | 51377.095 | 53494.4906 | 50076.8665 | 51873.9937 | 55560.4804 | 61563.2828 | 61888.2704 | 54167.31 | 61833.9958 | 76239.2502 | 677607.0975
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 18430.789 | 17654.4503 | 17125.6983 | 15088.1897 | 19447.2288 | 10514.0063 | 11429.5196 | 8656.7172 | 7151.7296 | 18552.69 | 7206.0042 | 880.7498 | 152137.7728 | 68 | 6 | 5.6667 | 0.5
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187
Derated capacity | kW | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
Fuel consumed in generation | litre | 22290.8259 | 22291.4883 | 22850.9069 | 22158.4224 | 22178.352 | 21974.96 | 22294.8 | 25648 | 18696 | 22278 | 20958 | 23894 | 267513.7554
Lubricating oil used | litre | 147.1266 | 146.7388 | 143.6157 | 151.8464 | 142.872 | 150.56 | 144.8 | 128 | 193 | 98 | 189 | 116 | 1751.5595
Number of consumer | number | 1045.0097 | 1045.0092 | 1045.0065 | 1045.0035 | 1045.0046 | 1045.0165 | 1045.0179 | 1045.0062 | 1044.9904 | 1044.9855 | 1045.0112 | 1045.0876 | 1045.0876
Station running time to generate | hr | [12 empty] | 0
Peak demand | kW | 226.7783 | 224.0956 | 222.082 | 222.4988 | 222.5347 | 221.4583 | 248 | 208 | 210 | 225 | 222.75 | 215 | 248
Minimum demand | kW | 65.1677 | 63.2866 | 62.8528 | 60.3024 | 60.3038 | 60.2604 | 84 | 52 | 60.25 | 45 | 60.3125 | 60 | 45
Fuel rate | kWh/ltr | 3.068 | 3.0718 | 3.0257 | 3.1264 | 3.1731 | 2.839 | 3.0477 | 2.7731 | 3.6947 | 3.3127 | 3.3504 | 3.2669 | 3.1336
|  | 0.0066003 | 0.0065827 | 0.0062849 | 0.0068528 | 0.006442 | 0.0068514 | 0.0064948 | 0.0049906 | 0.010323 | 0.004399 | 0.009018 | 0.0048548
TONGA POWER: TONGA 2002 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 3676694.8745 | 3357868.0858 | 3793392.3677 | 3602568.0011 | 3684671.619 | 3510940 | 3584228 | 3446724 | 3383133 | 3566261 | 3561549 | 3846675 | 43014704.9482
Power retained by licence | kWh | 60244.9973 | 58138.9648 | 66479.9233 | 63092.05 | 59510.96 | 64566.8826 | 51349.8333 | 69265.5515 | 65861.1 | 60980.9394 | 62092.3333 | 63371.3333 | 744954.869
Power supplied to customers | kWh | 3616449.8772 | 3299729.121 | 3726912.4444 | 3539475.9511 | 3625160.659 | 3446373.1174 | 3532878.1667 | 3377458.4485 | 3317271.9 | 3505280.0606 | 3499456.6667 | 3783303.6667 | 42269750.0792
Billing | kWh | 2441873.9112 | 2485030.6736 | 2729237.8618 | 2718068.0434 | 2583721.5148 | 2068035.9682 | 2738979.727 | 2476030.8556 | 3223478.0226 | 2558433.3614 | 2804818.2278 | 3258644.6603 | 32086352.8277
Transmission losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution losses | kWh | 1174575.966 | 814698.4474 | 997674.5826 | 821407.9077 | 1041439.1442 | 1378337.1492 | 793898.4397 | 901427.5929 | 93793.8774 | 946846.6992 | 694638.4388 | 524659.0063 | 10183397.2515
Unmetered read | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installed capacity | kW | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117
Derated capacity | kW | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5
Fuel consumed in generation | litre | 955919.0651 | 879226.1001 | 995271.7335 | 935911.764 | 946975.8522 | 898143.6636 | 928081.8909 | 895683.0727 | 878675.2 | 912843.0909 | 911616 | 989947 | 11128294.433
Lubricating oil used | litre | 2996.1005 | 3103.9289 | 2536.091 | 3284.2885 | 2744.3982 | 2415.4808 | 3266.7906 | 2999.3338 | 3413.4379 | 3095.2 | 1843.3636 | 3164.75 | 34863.1639
Number of consumer | number | 19574.4058 | 19554.4093 | 19604.0756 | 19622.5021 | 19611.2052 | 19598.7994 | 19455.4433 | 19434.4304 | 19902.0733 | 19733.0608 | 19543.4242 | 19524.3646 | 19902.1979
Station running time to generate | hr | 3307 | 3904.3333 | 4186.75 | 4084.7708 | 4063.7708 | 4014.5595 | 3887.5387 | 4416.2054 | 4053.6667 | 4183.8439 | 4054.8439 | 4763 | 48920.2831
Peak demand | kW | 7406.1838 | 7568.1098 | 7799.9936 | 7797.1773 | 7754.462 | 7728.7374 | 7819.5291 | 7487.5738 | 7673.1343 | 7991.879 | 7768.4582 | 8110.0158 | 8110.0158
Minimum demand | kW | 3551.5796 | 2418.1637 | 3594.8829 | 2521.5684 | 3156.0142 | 3496.1244 | 3285.7237 | 3250.5434 | 3272.5748 | 3196.3029 | 3339.3151 | 3615.6691 | 2418.1637
Fuel rate | kWh/ltr | 3.8462 | 3.8191 | 3.8114 | 3.8493 | 3.891 | 3.9091 | 3.862 | 3.8482 | 3.8503 | 3.9068 | 3.9069 | 3.8857 | 3.8653

## 2003
TOWER POWER LTD GENERATIONS FOR YEAR 2003
|  | 0.66695 | 0.73541 | 0.73533 | 0.7458 | 0.71041 | 0.59085 | 0.76665 | 0.71725 | 0.98299 | 0.72279 | 0.5696 | 0.84821
TONGA POWER: TONGATAPU 2003 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 3512182 | 3145896 | 3449266 | 3345233 | 3396862 | 3125481 | 3281651 | 3170242 | 3136378 | 3277591 | 3204789 | 3559132 | 39604703
Power retained by licence | kWh | 47638 | 42776 | 36922 | 46665 | 47542 | 46457 | 49283 | 47018 | 44658 | 40119 | 45189 | 47996 | 542263
Power supplied to customers | kWh | 3464544 | 3103120 | 3412344 | 3298568 | 3349320 | 3079024 | 3232368 | 3123224 | 3091720 | 3237472 | 3159600 | 3511136 | 39062440
Billing | kWh | 2310680 | 2282075 | 2509184 | 2460070 | 2379402 | 1819247 | 2478087 | 2240137 | 3039144 | 2340021 | 1799707 | 2978167 | 28635921
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 1153864 | 821045 | 903160 | 838498 | 969918 | 1259777 | 754281 | 883087 | 52576 | 897451 | 1359893 | 532969 | 10426519
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400
Derated capacity | kW | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000
Fuel consumed in generation | litre | 897772 | 761228 | 942072 | 871430 | 867622 | 793317 | 840299 | 768077 | 792808 | 835958 | 755917 | 905762 | 10032262
Lubricating oil used | litre | 3580 | 1816 | 2930 | 3862 | 2862 | 360 | 3370 | 2830 | 1826 | 2966 | 1880 | 2593 | 30875
Number of consumer | number | 15679 | 14417 | 11501 | 15365 | 15456 | 14343 | 14318 | 14291 | 14307 | 14351 | 14318 | 14228 | 15679
Station running time to generate | hr | 2188 | 2575 | 2899 | 2948 | 2652.5 | 2700 | 2872 | 2690.6429 | 2762.449 | 2916 | 2546 | 3190 | 32939.5918
Peak demand | kW | 6876 | 6805 | 6690 | 6972 | 6835.75 | 6815 | 6841 | 6669 | 6785 | 6780 | 6722 | 7423 | 7423
Minimum demand | kW | 932 | 3146 | 2089 | 3064 | 2307.75 | 3000 | 3030 | 2920 | 2296 | 3063 | 3120 | 3256 | 932
Fuel rate | kWh/ltr | 3.9121 | 4.1327 | 3.6614 | 3.8388 | 3.9151 | 3.9398 | 3.9053 | 4.1275 | 3.956 | 3.9208 | 4.2396 | 3.9294 | 3.9477
TONGA POWER : VAVA'U 2003 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 363440 | 327144 | 388246 | 385756 | 384088 | 331568 | 357750 | 368310 | 375516 | 404129 | 368361 | 397755 | 4452063
Power retained by licence | kWh | 18067 | 15794 | 18150 | 17738 | 16558 | 16558 | 16000 | 16000 | 19426 | 19025 | 19055 | 19085 | 211456
Power supplied to customers | kWh | 345373 | 311350 | 370096 | 368018 | 367530 | 315010 | 341750 | 352310 | 356090 | 385104 | 349306 | 378670 | 4240607
Billing | kWh | 257833 | 288150 | 251971 | 358372 | 262552 | 185998 | 287100 | 289528 | 328034 | 297995 | 343604 | 372360 | 3523497
Transmission losses | kWh
Distribution losses | kWh | 87540 | 23200 | 118125 | 9646 | 104978 | 129012 | 54650 | 62782 | 28056 | 87109 | 5702 | 6310 | 717110
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158
Derated capacity | kW | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1
Fuel consumed in generation | litre | 102419 | 88453 | 102987 | 103485 | 106490 | 91847 | 86414 | 71380 | 99331 | 106286 | 100385 | 107391 | 1166868
Lubricating oil used | litre | 135 | 153 | 162 | 416 | 352 | 317 | 317 | 267 | 418 | 445 | 366 | 489 | 3837
Number of consumer | number | 3192.9308 | 3192.9318 | 3192.9282 | 3192.9227 | 3192.9214 | 3192.9323 | 3192.9484 | 3192.9375 | 3192.907 | 3192.8899 | 3192.9135 | 3192.9973 | 3192.9973
Station running time to generate | hr | 2188 | 1812 | 2090 | 2099 | 2047.25 | 2012.0625 | 2099 | 2049.6161 | 1598 | 2668 | 2024 | 3460 | 26146.9286
Peak demand | kW | 859.879 | 861.8911 | 869.202 | 800 | 869.6883 | 879.0185 | 800 | 884.7778 | 897.3333 | 877 | 880 | 935 | 935
Minimum demand | kW | 367.8343 | 367.669 | 368.1591 | 367.6749 | 367.1728 | 369.6296 | 366.2222 | 365.6667 | 377 | 356 | 364 | 411 | 356
Fuel rate | kWh/ltr | 3.5486 | 3.6985 | 3.7699 | 3.7277 | 3.6068 | 3.61 | 4.14 | 5.1598 | 3.7805 | 3.8023 | 3.6695 | 3.7038 | 3.8154
TONGA POWER : HA'APAI 2003 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 108620 | 90940 | 96370 | 107980 | 109430 | 90740 | 101198 | 109207 | 102138 | 115737 | 93590 | 105500 | 1231450
Power retained by licence | kWh | 314 | 0 | 429 | 4406 | 0 | 0 | 0 | 5407 | 3834 | 4521 | 3266 | 3632 | 25809
Power supplied to customers | kWh | 108306 | 90940 | 95941 | 103574 | 109430 | 90740 | 101198 | 103800 | 98304 | 111216 | 90324 | 101868 | 1205641
Billing | kWh | 73447 | 65679 | 75513 | 82859.2 | 85304 | 69498 | 80285 | 86636 | 81006 | 88922 | 75313 | 81494.4 | 945956.6
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 34859 | 25261 | 20428 | 20714.8 | 24126 | 21242 | 20913 | 17164 | 17298 | 22294 | 15011 | 20373.6 | 259684.4
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
Derated capacity | kW | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4
Fuel consumed in generation | litre | 33507 | 26129 | 28486 | 24291 | 45962 | 32509 | 25400 | 28257 | 26465 | 29567 | 26011 | 28404 | 354988
Lubricating oil used | litre | 29 | 35 | 81 | 84 | 138 | 74 | 57 | 135 | 143 | 106 | 94 | 420 | 1396
Number of consumer | number | 984.1613 | 984.159 | 984.1546 | 984.1525 | 984.1583 | 984.1781 | 984.1652 | 984.1455 | 984.1281 | 984.1399 | 984.1933 | 984.2966 | 984.2966
Station running time to generate | hr | 824 | 741 | 711 | 835 | 777.75 | 663 | 975 | 789.5357 | 784.6122 | 1008 | 823 | 953 | 9884.898
Peak demand | kW | 252 | 217 | 196 | 265 | 232.5 | 262 | 255 | 252 | 260 | 262 | 263 | 263 | 265
Minimum demand | kW | 89.3459 | 90.0216 | 89.1846 | 88.9872 | 88.656 | 89.88 | 93.4 | 85 | 88 | 87 | 96 | 111 | 85
Fuel rate | kWh/ltr | 3.2417 | 3.4804 | 3.3831 | 4.4453 | 2.3809 | 2.7912 | 3.9842 | 3.8648 | 3.8594 | 3.9144 | 3.5981 | 3.7143 | 3.469
TONGA POWER: 'EUA 2003 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 80906 | 67848 | 74718 | 74898 | 83784 | 79434 | 83892 | 77454 | 77862 | 81348 | 76764 | 82866 | 941774
Power retained by licence | kWh | 2906 | 1128 | 1198 | 1218 | 1144 | 1274 | 1332 | 1294 | 1222 | 1348 | 1324 | 1346 | 16734
Power supplied to customers | kWh | 78000 | 66720 | 73520 | 73680 | 82640 | 78160 | 82560 | 76160 | 76640 | 80000 | 75440 | 81520 | 925040
Billing | kWh | 56770 | 49372.8 | 55140 | 57470.4 | 59524 | 64988 | 68474 | 66771 | 68701 | 59590 | 67566 | 80589 | 754956.2
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 21230 | 17347.2 | 18380 | 16209.6 | 23116 | 13172 | 14086 | 9389 | 7939 | 20410 | 7874 | 931 | 170083.8 | 64 | 6 | 5.3333 | 0.5
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187
Derated capacity | kW | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
Fuel consumed in generation | litre | 25013 | 21357 | 23542 | 22834 | 27704 | 26944 | 26563 | 25327 | 24825 | 24535 | 22295 | 25040 | 295979
Lubricating oil used | litre | 112 | 34 | 192 | 16 | 248 | 22 | 77 | 43 | 682 | 118 | 113 | 113 | 1770
Number of consumer | number | 1045.0179 | 1045.0062 | 1044.9904 | 1044.9855 | 1045.0112 | 1045.0876 | 1045.0263 | 1044.9365 | 1044.8956 | 1044.9562 | 1045.1648 | 1045.546 | 1045.546
Station running time to generate | hr | 980 | 837 | 995 | 969 | 1040 | 1043 | 1095 | 983 | 753 | 745 | 720 | 745 | 10905
Peak demand | kW | 224 | 268 | 226 | 265 | 245 | 233 | 244 | 238 | 230 | 240 | 240 | 262 | 268
Minimum demand | kW | 59 | 65 | 65 | 105 | 69 | 62 | 62 | 62 | 70 | 70 | 75 | 75 | 59
Fuel rate | kWh/ltr | 3.2346 | 3.1769 | 3.1738 | 3.2801 | 3.0243 | 2.9481 | 3.1582 | 3.0582 | 3.1364 | 3.3156 | 3.4431 | 3.3093 | 3.1819
TONGA POWER : TONGA 2003 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4065148 | 3631828 | 4008600 | 3913867 | 3974164 | 3627223 | 3824491 | 3725213 | 3691894 | 3878805 | 3743504 | 4145253 | 46229990
Power retained by licence | kWh | 68925 | 59698 | 56699 | 70027 | 65244 | 64289 | 66615 | 69719 | 69140 | 65013 | 68834 | 72059 | 796262
Power supplied to customers | kWh | 3996223 | 3572130 | 3951901 | 3843840 | 3908920 | 3562934 | 3757876 | 3655494 | 3622754 | 3813792 | 3674670 | 4073194 | 45433728
Billing | kWh | 2698730 | 2685276.8 | 2891808 | 2958771.6 | 2786782 | 2139731 | 2913946 | 2683072 | 3516885 | 2786528 | 2286190 | 3512610.4 | 33860330.8
Transmission losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution losses | kWh | 1297493 | 886853.2 | 1060093 | 885068.4 | 1122138 | 1423203 | 843930 | 972422 | 105869 | 1027264 | 1388480 | 560583.6 | 11573397.2
Unmetered read | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installed capacity | kW | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117 | 10117
Derated capacity | kW | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5 | 9612.5
Fuel consumed in generation | litre | 1058711 | 897167 | 1097087 | 1022040 | 1047778 | 944617 | 978676 | 893041 | 943429 | 996346 | 904608 | 1066597 | 11850097
Lubricating oil used | litre | 3856 | 2038 | 3365 | 4378 | 3600 | 773 | 3821 | 3275 | 3069 | 3635 | 2453 | 3615 | 37878
Number of consumer | number | 20901.11 | 19639.097 | 16723.0733 | 20587.0608 | 20678.0909 | 19565.1979 | 19540.1398 | 19513.0195 | 19528.9307 | 19572.9859 | 19540.2716 | 19450.84 | 20901.84
Station running time to generate | hr | 6180 | 5965 | 6695 | 6851 | 6517.5 | 6418.0625 | 7041 | 6512.7946 | 5898.0612 | 7337 | 6113 | 8348 | 79876.4184
Peak demand | kW | 8211.879 | 8151.8911 | 7981.202 | 8302 | 8182.9383 | 8189.0185 | 8140 | 8043.7778 | 8172.3333 | 8159 | 8105 | 8883 | 8883
Minimum demand | kW | 1448.1802 | 3668.6905 | 2611.3438 | 3625.6621 | 2832.5788 | 3521.5096 | 3551.6222 | 3432.6667 | 2831 | 3576 | 3655 | 3853 | 1448.1802
Fuel rate | kWh/ltr | 3.8397 | 4.0481 | 3.6539 | 3.8295 | 3.7929 | 3.8399 | 3.9078 | 4.1714 | 3.9133 | 3.893 | 4.1383 | 3.8864 | 3.9012
Note on C32: feleti ka wolfgramm: 380 from file
Note on E22: feleti ka wolfgramm: 379960
Note on E24: feleti ka wolfgramm: 361810
Note on N3: feleti ka wolfgramm: 1786748
Note on F49: feleti ka wolfgramm: Check

## 2004
TOWER POWER LTD GENERATIONS FOR YEAR 2004
TONGA POWER: TONGATAPU 2004 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 3495863 | 3531404 | 3768534 | 3244039 | 3456123 | 3301885 | 3383235 | 3398592 | 3115015 | 3438456 | 3403839 | 3854378 | 41391363
Power retained by licence | kWh | 47785 | 44802 | 48730 | 47189 | 42662 | 38426 | 40827 | 40650 | 38063 | 39766 | 46895 | 51268 | 527063
Power supplied to customers | kWh | 3448078 | 3486602 | 3719804 | 3196850 | 3413461 | 3263459 | 3342408 | 3357942 | 3076952 | 3398690 | 3356944 | 3803110 | 40864300
Billing | kWh | 2375095 | 2479055 | 2675169 | 2298300 | 2355707 | 2422661 | 2479005 | 2222465 | 2212913 | 2503308 | 2368850 | 2850966 | 29243494
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 1072983 | 1007547 | 1044635 | 898550 | 1057754 | 840798 | 863403 | 1135477 | 864039 | 895382 | 988094 | 952144 | 11620806
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800
Derated capacity | kW | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310
Fuel consumed in generation | litre | 903759 | 877501 | 953320 | 815506 | 851814 | 826763 | 856541 | 842727 | 793897 | 861071 | 859573 | 976275 | 10418747
Lubricating oil used | litre | 3481 | 2081 | 2862 | 3440 | 1955 | 3288 | 3155 | 1331 | 4050 | 2500 | 1912 | 2326 | 32381
Number of consumer | number | 14139 | 14268 | 14190 | 14133 | 14460 | 14518 | 14519 | 14553 | 14548 | 14582 | 14611 | 14468 | 14611
Station running time to generate | hr | 2966 | 2901 | 3307 | 3019 | 2926 | 2523 | 2431 | 2570 | 3028 | 3206 | 2047 | 3820 | 34744
Peak demand | kW | 6975 | 7247 | 7164 | 6700 | 6794 | 7007 | 7046 | 6927 | 6792 | 7076 | 7065 | 7627 | 7627
Minimum demand | kW | 3088 | 3725 | 3515 | 3097 | 2695 | 3205 | 2993 | 3061 | 3042 | 3190 | 3325 | 3326 | 2695
Fuel rate | kWh/ltr | 3.8681 | 4.0244 | 3.9531 | 3.9779 | 4.0574 | 3.9938 | 3.9499 | 4.0329 | 3.9237 | 3.9932 | 3.9599 | 3.948 | 3.9728
TONGA POWER : VAVA'U 2004 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 397495 | 375385 | 396773 | 369847 | 411122 | 459544 | 412724 | 407203 | 385314 | 419522 | 385991 | 414469 | 4835389
Power retained by licence | kWh | 18865 | 21665 | 15993 | 19087 | 19952 | 20874 | 19604 | 19993 | 19444 | 20722 | 18891 | 20669 | 235759
Power supplied to customers | kWh | 378630 | 353720 | 380780 | 350760 | 391170 | 438670 | 393120 | 387210 | 365870 | 398800 | 367100 | 393800 | 4599630
Billing | kWh | 403166 | 291644 | 422134 | 465496 | 351459 | 327955 | 395943 | 377251 | 328195 | 275538 | 295113 | 415325 | 4349219
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | -24536 | 62076 | -41354 | -114736 | 39711 | 110715 | -2823 | 9959 | 37675 | 123262 | 71987 | -21525 | 250411
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158
Derated capacity | kW | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1
Fuel consumed in generation | litre | 108850 | 100218 | 107019 | 98304 | 108749 | 120408 | 109697 | 107964 | 100861 | 110648 | 101327 | 109716 | 1283761
Lubricating oil used | litre | 427 | 403 | 406 | 458 | 432 | 440 | 452 | 425 | 312 | 470 | 475 | 405 | 5105
Number of consumer | number | 3192.9484 | 3192.9375 | 3192.907 | 3192.8899 | 3192.9135 | 3192.9973 | 3193.0453 | 3192.8722 | 3192.7238 | 3192.787 | 3193.0556 | 3193.5 | 3193.5
Station running time to generate | hr | 2098 | 1896 | 2076 | 1883 | 2130 | 2489 | 2190 | 2136 | 2079 | 2200 | 2108 | 2164 | 25449
Peak demand | kW | 852 | 856 | 854 | 872 | 1085 | 1112 | 920 | 922 | 918 | 920 | 912 | 925 | 1112
Minimum demand | kW | 368 | 302 | 380 | 385 | 476 | 575 | 411 | 408 | 398 | 410 | 408 | 412 | 302
Fuel rate | kWh/ltr | 3.6518 | 3.7457 | 3.7075 | 3.7623 | 3.7805 | 3.8166 | 3.7624 | 3.7717 | 3.8202 | 3.7915 | 3.8094 | 3.7777 | 3.7666
TONGA POWER : HA'APAI 2004 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 107007 | 106687 | 117036 | 110210 | 111940 | 103417 | 106519 | 107432 | 99175 | 110239 | 110239 | 108813 | 1298714
Power retained by licence | kWh | 4023 | 4579 | 4836 | 4718 | 4840 | 4261 | 3931 | 3788 | 2911 | 3883 | 3883 | 4041 | 49694
Power supplied to customers | kWh | 102984 | 102108 | 112200 | 105492 | 107100 | 99156 | 102588 | 103644 | 96264 | 106356 | 106356 | 104772 | 1249020
Billing | kWh | 102303 | 76981 | 83556 | 92218 | 94479 | 81719 | 81145 | 86973 | 82151 | 79306 | 83141 | 96830 | 1040802
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 681 | 25127 | 28644 | 13274 | 12621 | 17437 | 21443 | 16671 | 14113 | 27050 | 23215 | 7942 | 208218
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
Derated capacity | kW | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4
Fuel consumed in generation | litre | 28819 | 27903 | 31094 | 29409 | 29226 | 27485 | 28129 | 28662 | 26672 | 29442 | 29442 | 29415 | 345698
Lubricating oil used | litre | 122 | 304 | 126 | 150 | 130 | 134 | 120 | 156 | 125 | 306 | 306 | 130 | 2109
Number of consumer | number | 984.1652 | 984.1455 | 984.1281 | 984.1399 | 984.1933 | 984.2966 | 984.0876 | 984.0275 | 984.0235 | 984.2106 | 984.5139 | 984.9167 | 984.9167
Station running time to generate | hr | 953 | 920 | 1047 | 950 | 962 | 910 | 939 | 936 | 885 | 922 | 922 | 937 | 11283
Peak demand | kW | 279 | 263 | 260 | 254 | 246 | 236 | 284 | 276 | 256 | 256 | 256 | 286 | 286
Minimum demand | kW | 85 | 88 | 49 | 47 | 47 | 47 | 46 | 86 | 71 | 100 | 100 | 86 | 46
Fuel rate | kWh/ltr | 3.7131 | 3.8235 | 3.7639 | 3.7475 | 3.8302 | 3.7627 | 3.7868 | 3.7482 | 3.7183 | 3.7443 | 3.7443 | 3.6992 | 3.7568
TONGA POWER: 'EUA 2004 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 81060 | 75750 | 81960 | 76992 | 79812 | 77766 | 81636 | 84918 | 77232 | 78767 | 82286 | 96716 | 974895
Power retained by licence | kWh | 1300 | 1830 | 1960 | 1712 | 1412 | 1206 | 1316 | 1398 | 1472 | 5579 | 5798 | 7016 | 31999
Power supplied to customers | kWh | 79760 | 73920 | 80000 | 75280 | 78400 | 76560 | 80320 | 83520 | 75760 | 73188 | 76488 | 89700 | 942896
Billing | kWh | 80589 | 59502 | 61838 | 68164 | 71379 | 64368 | 64116 | 74712 | 65613 | 62925 | 71975 | 66243 | 811424
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | -829 | 14418 | 18162 | 7116 | 7021 | 12192 | 16204 | 8808 | 10147 | 10263 | 4513 | 23457 | 131472 | 60 | 7 | 5 | 0.58333
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187
Derated capacity | kW | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
Fuel consumed in generation | litre | 23573 | 21733 | 23846 | 20552 | 25497 | 21080 | 23251 | 25000 | 21818 | 21069 | 21510 | 24724 | 273653
Lubricating oil used | litre | 102 | 114 | 119 | 121 | 119 | 119 | 117 | 129 | 119 | 456 | 99 | 128 | 1742
Number of consumer | number | 1045.0263 | 1044.9365 | 1044.8956 | 1044.9562 | 1045.1648 | 1045.546 | 1044.6585 | 1044.3978 | 1044.6505 | 1045.3194 | 1046.4167 | 1047.8333 | 1047.8333
Station running time to generate | hr | 741 | 693 | 742 | 719 | 742 | 719 | 741 | 742 | 719 | 771 | 810 | 889 | 9028
Peak demand | kW | 240 | 220 | 240 | 220 | 220 | 220 | 220 | 220 | 230 | 265 | 257 | 275 | 275
Minimum demand | kW | 75 | 75 | 75 | 75 | 65 | 68 | 75 | 75 | 69 | 80 | 76 | 84 | 65
Fuel rate | kWh/ltr | 3.4387 | 3.4855 | 3.4371 | 3.7462 | 3.1303 | 3.6891 | 3.5111 | 3.3967 | 3.5398 | 3.7385 | 3.8255 | 3.9118 | 3.5625
TONGA POWER : TONGA 2004 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4081425 | 4089226 | 4364303 | 3801088 | 4058997 | 3942612 | 3984114 | 3998145 | 3676736 | 4046984 | 3982355 | 4474376 | 48500361
Power retained by licence | kWh | 71973 | 72876 | 71519 | 72706 | 68866 | 64767 | 65678 | 65829 | 61890 | 69950 | 75467 | 82994 | 844515
Power supplied to customers | kWh | 4009452 | 4016350 | 4292784 | 3728382 | 3990131 | 3877845 | 3918436 | 3932316 | 3614846 | 3977034 | 3906888 | 4391382 | 47655846
Billing | kWh | 2961153 | 2907182 | 3242697 | 2924178 | 2873024 | 2896703 | 3020209 | 2761401 | 2688872 | 2921077 | 2819079 | 3429364 | 35444939
Transmission losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution losses | kWh | 1048299 | 1109168 | 1050087 | 804204 | 1117107 | 981142 | 898227 | 1170915 | 925974 | 1055957 | 1087809 | 962018 | 12210907
Unmetered read | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installed capacity | kW | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517
Derated capacity | kW | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5
Fuel consumed in generation | litre | 1065001 | 1027355 | 1115279 | 963771 | 1015286 | 995736 | 1017618 | 1004353 | 943248 | 1022230 | 1011852 | 1140130 | 12321859
Lubricating oil used | litre | 4132 | 2902 | 3513 | 4169 | 2636 | 3981 | 3844 | 2041 | 4606 | 3732 | 2792 | 2989 | 41337
Number of consumer | number | 19361.1398 | 19490.0195 | 19411.9307 | 19354.9859 | 19682.2716 | 19740.84 | 19740.7914 | 19774.2974 | 19769.3978 | 19804.3171 | 19834.9861 | 19694.25 | 19837.25
Station running time to generate | hr | 6758 | 6410 | 7172 | 6571 | 6760 | 6641 | 6301 | 6384 | 6711 | 7099 | 5887 | 7810 | 80504
Peak demand | kW | 8346 | 8586 | 8518 | 8046 | 8345 | 8575 | 8470 | 8345 | 8196 | 8517 | 8490 | 9113 | 9113
Minimum demand | kW | 3616 | 4190 | 4019 | 3604 | 3283 | 3895 | 3525 | 3630 | 3580 | 3780 | 3909 | 3908 | 3283
Fuel rate | kWh/ltr | 3.8323 | 3.9803 | 3.9132 | 3.944 | 3.9979 | 3.9595 | 3.9151 | 3.9808 | 3.898 | 3.959 | 3.9357 | 3.9244 | 3.9361
Note on C3: feleti ka wolfgramm: 1499914
Note on D3: feleti ka wolfgramm: 1516672
Note on L3: feleti ka wolfgramm: 1751171
Note on M3: feleti ka wolfgramm: 2118841

## 2005
TOWER POWER LTD GENERATIONS FOR YEAR 2005
TONGA POWER: TONGATAPU 2005 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 3961381 | 3525032 | 3845799 | 3575578 | 3541591 | 3422947 | 3452917 | 3443077 | 3521276 | 3722498 | 3833817 | 4178951 | 44024864
Power retained by licence | kWh | 48567 | 46960 | 51523 | 48414 | 49603 | 45521 | 41418 | 49281 | 50279 | 52088 | 48290 | 52596 | 584540
Power supplied to customers | kWh | 3912814 | 3478072 | 3794276 | 3527164 | 3491988 | 3377426 | 3411499 | 3393796 | 3470997 | 3670410 | 3785527 | 4126355 | 43440324
Billing | kWh | 2853625 | 2499030 | 3088814 | 2746098 | 2753032 | 2675855 | 2557464 | 2972969 | 2407635 | 2535608 | 2664975 | 2792386 | 32547491
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 1059189 | 979042 | 705462 | 781066 | 738956 | 701571 | 854035 | 420827 | 1063362 | 1134802 | 1120552 | 1333969 | 10892833
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800 | 9800
Derated capacity | kW | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310 | 9310
Fuel consumed in generation | litre | 986116 | 895039 | 971821 | 905202 | 902064 | 863875 | 864305 | 866298 | 890791 | 943143 | 970264 | 1058915 | 11117833
Lubricating oil used | litre | 2653 | 3364 | 2132 | 2324 | 3100 | 1778 | 2326 | 1822 | 2861 | 1460 | 3138 | 2325 | 29283
Number of consumer | number | 14615 | 14820 | 14882 | 14938 | 14990 | 14963 | 14923 | 14700 | 14742 | 14792 | 14750 | 14765 | 14990
Station running time to generate | hr | 3616 | 2592.375 | 2553.4821 | 1841 | 1892 | 2136 | 2975 | 2447 | 2916 | 2916 | 2588.4857 | 2588.4857 | 31061.8286
Peak demand | kW | 7357 | 7354 | 7579 | 7448 | 7315 | 7196 | 7284 | 7094 | 7521 | 7521 | 7657 | 8258 | 8258
Minimum demand | kW | 2940 | 3714 | 3547 | 3308 | 2718 | 3287 | 3364 | 3297 | 3438 | 3438 | 3129 | 3129 | 2718
Fuel rate | kWh/ltr | 4.0172 | 3.9384 | 3.9573 | 3.95 | 3.9261 | 3.9623 | 3.995 | 3.9745 | 3.953 | 3.9469 | 3.9513 | 3.9464 | 3.9598
TONGA POWER : VAVA'U 2005 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 446591 | 390601 | 418914 | 400137 | 436708 | 389627 | 395979 | 408489 | 410529 | 430128 | 421340 | 478583 | 5027626
Power retained by licence | kWh | 21651 | 19551 | 21774 | 20007 | 20968 | 19337 | 19129 | 19839 | 19899 | 20158 | 19520 | 22243 | 244076
Power supplied to customers | kWh | 424940 | 371050 | 397140 | 380130 | 415740 | 370290 | 376850 | 388650 | 390630 | 409970 | 401820 | 456340 | 4783550
Billing | kWh | 328816 | 322948 | 323216 | 351072 | 326848 | 318772 | 324192 | 331982 | 375688 | 322639 | 316332 | 354949 | 3997454
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 96124 | 48102 | 73924 | 29058 | 88892 | 51518 | 52658 | 56668 | 14942 | 87331 | 85488 | 101391 | 786096
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158
Derated capacity | kW | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1
Fuel consumed in generation | litre | 986116 | 104091 | 110765 | 106338 | 116682 | 103487 | 105349 | 109110 | 109446 | 115553 | 112833 | 128298 | 2208068
Lubricating oil used | litre | 2653 | 573 | 323 | 400 | 416 | 420 | 522 | 343 | 397 | 437 | 440 | 439 | 7363
Number of consumer | number | 3193.0453 | 3192.8722 | 3192.7238 | 3192.787 | 3193.0556 | 3193.5 | 3193.3333 | 3191.8333 | 3191.8333 | 3193.1667 | 3194.6667 | 3196.1667 | 3196.1667
Station running time to generate | hr | 2385 | 2199 | 2382 | 2261 | 2484 | 2198 | 3472 | 2108 | 1998 | 2436 | 2204 | 2590 | 28717
Peak demand | kW | 972 | 964 | 945 | 940 | 982 | 920 | 926 | 905 | 913 | 975 | 975 | 1018 | 1018
Minimum demand | kW | 427 | 422 | 418 | 415 | 418 | 418 | 409 | 405 | 411 | 415 | 418 | 454 | 405
Fuel rate | kWh/ltr | 0.45288 | 3.7525 | 3.782 | 3.7629 | 3.7427 | 3.765 | 3.7587 | 3.7438 | 3.751 | 3.7223 | 3.7342 | 3.7302 | 2.2769
TONGA POWER : HA'APAI 2005 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 117639 | 110101 | 113176 | 116012 | 115887 | 112315 | 114551 | 113898 | 115639 | 123687 | 121138 | 133000 | 1407043
Power retained by licence | kWh | 4221 | 3661 | 4072 | 4472 | 4863 | 4723 | 4943 | 4506 | 5131 | 4983 | 4354 | 5596 | 55525
Power supplied to customers | kWh | 113418 | 106440 | 109104 | 111540 | 111024 | 107592 | 109608 | 109392 | 110508 | 118704 | 116784 | 127404 | 1351518
Billing | kWh | 90739 | 83164 | 99513 | 101107 | 92669 | 87506 | 92909 | 91267 | 97359 | 95922 | 96639 | 116717 | 1145511
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 22679 | 23276 | 9591 | 10433 | 18355 | 20086 | 16699 | 18125 | 13149 | 22782 | 20145 | 10687 | 206007
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
Derated capacity | kW | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4
Fuel consumed in generation | litre | 32014 | 30378 | 30632 | 31213 | 29695 | 29461 | 29926 | 30936 | 30748 | 33367 | 32628 | 36713 | 377711
Lubricating oil used | litre | 178 | 148 | 173 | 173 | 163 | 165 | 148 | 143 | 176 | 154 | 172 | 178 | 1971
Number of consumer | number | 984.0876 | 984.0275 | 984.0235 | 984.2106 | 984.5139 | 984.9167 | 982.8333 | 983.6667 | 984 | 985.3333 | 986.3333 | 987.3333 | 987.3333
Station running time to generate | hr | 1103 | 1053 | 1107 | 1116 | 1040 | 979 | 1253 | 990 | 1021 | 1138 | 1288 | 1353 | 13441
Peak demand | kW | 286 | 260 | 275 | 275 | 265 | 275 | 270 | 269 | 271 | 272 | 273 | 305 | 305
Minimum demand | kW | 97 | 92 | 90 | 100 | 98 | 100 | 108 | 105 | 100 | 100 | 100 | 110 | 90
Fuel rate | kWh/ltr | 3.6746 | 3.6244 | 3.6947 | 3.7168 | 3.9026 | 3.8123 | 3.8278 | 3.6817 | 3.7609 | 3.7069 | 3.7127 | 3.6227 | 3.7252
TONGA POWER: 'EUA 2005 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 93586 | 87039 | 99396 | 71160 | 91865 | 89817 | 95389 | 89707 | 89461 | 96111 | 94549 | 103308 | 1101388
Power retained by licence | kWh | 3118 | 2019 | 2531 | 2556 | 11213 | 5637 | 9793 | 5299 | 4513 | 7263 | 11245 | 7716 | 72903
Power supplied to customers | kWh | 90468 | 85020 | 96865 | 68604 | 80652 | 84180 | 85596 | 84408 | 84948 | 88848 | 83304 | 95592 | 1028485
Billing | kWh | 71608 | 67727 | 71354 | 75559 | 66592 | 70619 | 73092 | 70020 | 77492 | 71638 | 85902 | 73354 | 874957
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 18860 | 17293 | 25511 | -6955 | 14060 | 13561 | 12504 | 14388 | 7456 | 17210 | -2598 | 22238 | 153528 | 54 | 7 | 4.5 | 0.58333
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187
Derated capacity | kW | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
Fuel consumed in generation | litre | 25072 | 24533 | 28885 | 19725 | 25515 | 24992 | 24279 | 23805 | 24799 | 25511 | 24300 | 25690 | 297106
Lubricating oil used | litre | 123 | 118 | 155 | 160 | 155 | 155 | 165 | 170 | 176 | 160 | 145 | 170 | 1852
Number of consumer | number | 1044.6585 | 1044.3978 | 1044.6505 | 1045.3194 | 1046.4167 | 1047.8333 | 1039.3333 | 1042.8333 | 1046.1667 | 1049.3333 | 1053 | 1056.3333 | 1056.3333
Station running time to generate | hr | 885 | 842 | 989 | 731 | 985 | 951 | 949 | 951 | 928 | 970 | 937 | 992 | 11110
Peak demand | kW | 275 | 270 | 275 | 279 | 270 | 270 | 270 | 270 | 270 | 270 | 275 | 285 | 285
Minimum demand | kW | 84 | 91 | 91 | 94 | 86 | 86 | 86 | 80 | 86 | 85 | 90 | 85 | 80
Fuel rate | kWh/ltr | 3.7327 | 3.5478 | 3.4411 | 3.6076 | 3.6004 | 3.5938 | 3.9289 | 3.7684 | 3.6074 | 3.7674 | 3.8909 | 4.0213 | 3.7071
TONGA POWER : TONGA 2005 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4619197 | 4112773 | 4477285 | 4162887 | 4186051 | 4014706 | 4058836 | 4055171 | 4136905 | 4372424 | 4470844 | 4893842 | 51560921
Power retained by licence | kWh | 77557 | 72191 | 79900 | 75449 | 86647 | 75218 | 75283 | 78925 | 79822 | 84492 | 83409 | 88151 | 957044
Power supplied to customers | kWh | 4541640 | 4040582 | 4397385 | 4087438 | 4099404 | 3939488 | 3983553 | 3976246 | 4057083 | 4287932 | 4387435 | 4805691 | 50603877
Billing | kWh | 3344788 | 2972869 | 3582897 | 3273836 | 3239141 | 3152752 | 3047657 | 3466238 | 2958174 | 3025807 | 3163848 | 3337406 | 38565413
Transmission losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution losses | kWh | 1196852 | 1067713 | 814488 | 813602 | 860263 | 786736 | 935896 | 510008 | 1098909 | 1262125 | 1223587 | 1468285 | 12038464
Unmetered read | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installed capacity | kW | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517 | 11517
Derated capacity | kW | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5 | 10922.5
Fuel consumed in generation | litre | 2029318 | 1054041 | 1142103 | 1062478 | 1073956 | 1021815 | 1023859 | 1030149 | 1055784 | 1117574 | 1140025 | 1249616 | 14000718
Lubricating oil used | litre | 5607 | 4203 | 2783 | 3057 | 3834 | 2518 | 3161 | 2478 | 3610 | 2211 | 3895 | 3112 | 40469
Number of consumer | number | 19836.7914 | 20041.2974 | 20103.3978 | 20160.3171 | 20213.9861 | 20189.25 | 20138.5 | 19918.3333 | 19964 | 20019.8333 | 19984 | 20004.8333 | 20229.8333
Station running time to generate | hr | 7989 | 6686.375 | 7031.4821 | 5949 | 6401 | 6264 | 8649 | 6496 | 6863 | 7460 | 7017.4857 | 7523.4857 | 84329.8286
Peak demand | kW | 8890 | 8848 | 9074 | 8942 | 8832 | 8661 | 8750 | 8538 | 8975 | 9038 | 9180 | 9866 | 9866
Minimum demand | kW | 3548 | 4319 | 4146 | 3917 | 3320 | 3891 | 3967 | 3887 | 4035 | 4038 | 3737 | 3778 | 3320
Fuel rate | kWh/ltr | 2.2762 | 3.9019 | 3.9202 | 3.9181 | 3.8978 | 3.929 | 3.9643 | 3.9365 | 3.9183 | 3.9124 | 3.9217 | 3.9163 | 3.6827
Note on G3: feleti ka wolfgramm: 1903133

## 2006
TOWER POWER LTD GENERATIONS FOR YEAR 2006
|  | 0.50972 | 0.44148 | 0.36339 | 0.47672 | 0.46188 | 0.40031 | 0.46048 | 0.46781 | 0.38711 | 0.42771 | 0.43948 | 0.43255
TONGA POWER: TONGATAPU 2006 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4249941 | 3484053 | 4477261 | 4396890 | 3989057 | 3714904 | 3716492 | 3809054 | 3715461 | 3876886 | 3698458 | 3777814 | 46906271
Power retained by licence | kWh | 52233 | 53306 | 53306 | 73455 | 53396 | 57326 | 43730 | 50916 | 49339 | 149584 | 88196 | 50512 | 775299
Power supplied to customers | kWh | 4197708 | 3430747 | 4423955 | 4323435 | 3935661 | 3657578 | 3672762 | 3758138 | 3666122 | 3727302 | 3610262 | 3727302 | 46130972
Billing | kWh | 3292876.0619 | 3041545.08 | 3699448 | 3240232 | 3277637 | 3746627.63 | 3023838 | 3483168.25 | 2799973.79 | 3016133 | 3012396 | 3325093 | 38958967.8119
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 904831.9381 | 389201.92 | 724507 | 1083203 | 658024 | -89049.63 | 648924 | 274969.75 | 866148.21 | 711169 | 597866 | 402209 | 7172004.1881
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680
Derated capacity | kW | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046
Fuel consumed in generation | litre | 1070657 | 900847 | 1120128 | 1033456 | 982514.0909 | 998611 | 960394 | 937144 | 952187 | 984011 | 911086 | 939134 | 11790169.0909
Lubricating oil used | litre | 4496 | 2832 | 3520 | 3662 | 2895.8182 | 2110 | 2740 | 2417 | 4671 | 2601 | 1815 | 990 | 34749.8182
Number of consumer | number | 14648 | 14837 | 14942 | 14973 | 14947 | 14969 | 15009 | 15047 | 14975 | 15179 | 15210 | 15232 | 15232
Station running time to generate | hr | 4919 | 3049.9959 | 3060.7096 | 3148.3824 | 3544.522 | 3544.522 | 3544.522 | 3315.4423 | 3359.6834 | 2398 | 3388.478 | 3235.4258 | 40508.6834
Peak demand | kW | 7918 | 7896 | 8374 | 8206 | 7932 | 7699 | 7831 | 7845 | 7866 | 7753 | 7932 | 7932 | 8374
Minimum demand | kW | 4036 | 3485.963 | 3043 | 3912 | 3663.6667 | 3082 | 3606 | 3670 | 3045 | 3316 | 3485.963 | 3430.9593 | 3043
Fuel rate | kWh/ltr | 3.9695 | 3.8675 | 3.9971 | 4.2545 | 4.0601 | 3.7201 | 3.8698 | 4.0645 | 3.902 | 3.9399 | 4.0594 | 4.0227 | 3.9784
TONGA POWER : VAVA'U 2006 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 448804 | 411462 | 487537 | 455049 | 446293 | 438467 | 450112 | 461154 | 443703 | 449341 | 419720 | 454684 | 5366326
Power retained by licence | kWh | 20964 | 19592 | 23877 | 19419 | 20863 | 20037 | 20102 | 20484 | 20113 | 20331 | 19300 | 31274 | 256356
Power supplied to customers | kWh | 427840 | 391870 | 463660 | 435630 | 425430 | 418430 | 430010 | 440670 | 423590 | 429010 | 400420 | 423410 | 5109970
Billing | kWh | 354949 | 345989 | 348861 | 394376 | 350600 | 358860 | 340233 | 360316 | 395967 | 388665 | 346503 | 295764 | 4281083
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 72891 | 45881 | 114799 | 41254 | 74830 | 59570 | 89777 | 80354 | 27623 | 40345 | 53917 | 127646 | 828887 | 743 | 61.9167
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158 | 1158
Derated capacity | kW | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 | 1100.1 |  |  | mafi.maka@gmail.com
Fuel consumed in generation | litre | 119074 | 109655 | 128765 | 121787 | 121039 | 116885 | 120093 | 124045 | 123222 | 123984 | 113994 | 121543 | 1444086
Lubricating oil used | litre | 421 | 440 | 490 | 565 | 615 | 505 | 458 | 522 | 533 | 581 | 437 | 530 | 6097
Number of consumer | number | 3193 | 3194 | 3195 | 3191 | 3193 | 3194 | 3193 | 3185 | 3195 | 3199 | 3202 | 3203 | 3203
Station running time to generate | hr | 2414 | 2206 | 2584 | 2464 | 2367 | 2305 | 2262 | 2926 | 5350 | 3912 | 4142 | 4783 | 37715
Peak demand | kW | 987 | 985 | 992 | 995 | 986 | 1045 | 1018 | 1005 | 1018 | 1005 | 1011 | 1087 | 1087
Minimum demand | kW | 465 | 455 | 450 | 456 | 436 | 456 | 420 | 415 | 412 | 413 | 415 | 465 | 412
Fuel rate | kWh/ltr | 3.7691 | 3.7523 | 3.7863 | 3.7364 | 3.6872 | 3.7513 | 3.748 | 3.7176 | 3.6008 | 3.6242 | 3.6819 | 3.7409 | 3.7161
TONGA POWER : HA'APAI 2006 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 131428 | 114791 | 141274 | 135624 | 155411 | 179053 | 132738 | 134861 | 128175 | 138159 | 127824 | 138993 | 1658331
Power retained by licence | kWh | 5332 | 3923 | 4798 | 4668 | 5639 | 52681 | 8298 | 5645 | 5307 | 5847 | 5232 | 5901 | 113271
Power supplied to customers | kWh | 126096 | 110868 | 136476 | 130956 | 149772 | 126372 | 124440 | 129216 | 122868 | 132312 | 122592 | 133092 | 1545060
Billing | kWh | 101974 | 95604 | 120101 | 109997 | 120430 | 111604 | 100004 | 118634 | 105003 | 105973 | 115079 | 108370 | 1312773
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 24122 | 15264 | 16375 | 20959 | 29342 | 14768 | 24436 | 10582 | 17865 | 26339 | 7513 | 24722 | 232287
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
Derated capacity | kW | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4
Fuel consumed in generation | litre | 35189 | 31117 | 39002 | 37169 | 41232 | 35459 | 35244 | 36133 | 34818 | 37606 | 35636 | 37793 | 436398
Lubricating oil used | litre | 183 | 236 | 248 | 174 | 237 | 248 | 182 | 176 | 212 | 422 | 154 | 242 | 2714
Number of consumer | number | 978 | 979 | 983 | 982 | 984 | 985 | 984 | 984 | 985 | 990 | 990 | 991 | 991
Station running time to generate | hr | 1374 | 1192 | 1459 | 1411 | 1463 | 1342 | 1307 | 1359 | 1306 | 1404 | 1299 | 1420 | 16336
Peak demand | kW | 292 | 278 | 305 | 315 | 345 | 315 | 310 | 308 | 302 | 324 | 312 | 326 | 345
Minimum demand | kW | 107 | 95 | 129 | 129 | 145 | 138 | 129 | 130 | 129 | 130 | 107 | 120 | 95
Fuel rate | kWh/ltr | 3.7349 | 3.689 | 3.6222 | 3.6488 | 3.7692 | 5.0496 | 3.7663 | 3.7323 | 3.6813 | 3.6739 | 3.5869 | 3.6777 | 3.8
TONGA POWER: 'EUA 2006 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 91691 | 81370 | 106638 | 94146 | 94147 | 95673 | 100371 | 98378 | 98754 | 94901 | 86705 | 101858 | 1144632
Power retained by licence | kWh | 935 | 4294 | 10194 | 2490 | 2323 | 8253 | 6315 | 4238 | 441 | 4865 | 1949 | 6866 | 53163
Power supplied to customers | kWh | 90756 | 77076 | 96444 | 91656 | 91824 | 87420 | 94056 | 94140 | 78636 | 90036 | 84756 | 94992 | 1071792
Billing | kWh | 93479 | 68669 | 78583 | 72484 | 77888 | 76100 | 72615 | 76715 | 72256 | 78027 | 72470 | 85753 | 925039
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | -2723 | 8407 | 17861 | 19172 | 13936 | 11320 | 21441 | 17425 | 6380 | 12009 | 12286 | 9239 | 146753 | 63 | 6 | 5.25 | 0.5
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187
Derated capacity | kW | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
Fuel consumed in generation | litre | 25360 | 22143 | 27475 | 25508 | 25832 | 24557 | 27124 | 25640 | 24873 | 27203 | 25710 | 28430 | 309855
Lubricating oil used | litre | 190 | 170 | 160 | 160 | 160 | 160 | 180 | 185 | 180 | 165 | 170 | 190 | 2070
Number of consumer | number | 1038 | 1029 | 1034 | 1037 | 1043 | 1046 | 1047 | 1050 | 1054 | 1056 | 1065 | 1066 | 1066
Station running time to generate | hr | 995 | 869 | 1076 | 1004 | 990 | 934 | 998 | 1015 | 928 | 1062 | 983 | 1147 | 12001
Peak demand | kW | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 275 | 275
Minimum demand | kW | 85 | 85 | 86 | 85 | 86 | 85 | 85 | 89 | 89 | 90 | 85 | 96 | 85
Fuel rate | kWh/ltr | 3.6156 | 3.6748 | 3.8813 | 3.6908 | 3.6446 | 3.896 | 3.7004 | 3.8369 | 3.9703 | 3.4886 | 3.3724 | 3.5828 | 3.6941
|  | 0.0074921 | 0.0076774 | 0.0058235 | 0.0062725 | 0.0061939 | 0.0065155 | 0.0066362 | 0.0072153 | 0.0072368 | 0.0060655 | 0.0066122 | 0.0066831
TONGA POWER : TONGA 2006 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4921864 | 4091676 | 5212710 | 5081709 | 4684908 | 4428097 | 4399713 | 4503447 | 4386093 | 4559287 | 4332707 | 4473349 | 55075560
Power retained by licence | kWh | 79464 | 81115 | 92175 | 100032 | 82221 | 138297 | 78445 | 81283 | 75200 | 180627 | 114677 | 94553 | 1198089
Power supplied to customers | kWh | 4842400 | 4010561 | 5120535 | 4981677 | 4602687 | 4289800 | 4321268 | 4422164 | 4291216 | 4378660 | 4218030 | 4378796 | 53857794
Billing | kWh | 3843278.0619 | 3551807.08 | 4246993 | 3817089 | 3826555 | 4293191.63 | 3536690 | 4038833.25 | 3373199.79 | 3588798 | 3546448 | 3814980 | 45477862.8119
Transmission losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution losses | kWh | 999121.9381 | 458753.92 | 873542 | 1164588 | 776132 | -3391.63 | 784578 | 383330.75 | 918016.21 | 789862 | 671582 | 563816 | 8379931.1881
Unmetered read | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installed capacity | kW | 0 | 14397 | 14397 | 14397 | 14397 | 14397 | 14397 | 14397 | 14397 | 14397 | 14397 | 14397 | 14397
Derated capacity | kW | 13658.5 | 13658.5 | 13658.5 | 13658.5 | 13658.5 | 13658.5 | 13658.5 | 13658.5 | 13658.5 | 13658.5 | 13658.5 | 13658.5 | 13658.5
Fuel consumed in generation | litre | 1250280 | 1063762 | 1315370 | 1217920 | 1170617.0909 | 1175512 | 1142855 | 1122962 | 1135100 | 1172804 | 1086426 | 1126900 | 13980508.0909
Lubricating oil used | litre | 5290 | 3678 | 4418 | 4561 | 3907.8182 | 3023 | 3560 | 3300 | 5596 | 3769 | 2576 | 1952 | 45630.8182
Number of consumer | number | 19857 | 20039 | 20154 | 20183 | 20167 | 20194 | 20233 | 20266 | 20209 | 20424 | 20467 | 20492 | 20492 | 15983.76
Station running time to generate | hr | 9702 | 7316.9959 | 8179.7096 | 8027.3824 | 8364.522 | 8125.522 | 8111.522 | 8615.4423 | 10943.6834 | 8776 | 9812.478 | 10585.4258 | 106560.6834
Peak demand | kW | 9467 | 9429 | 9941 | 9786 | 9533 | 9329 | 9429 | 9428 | 9456 | 9352 | 9525 | 9620 | 9941
Minimum demand | kW | 4693 | 4120.963 | 3708 | 4582 | 4330.6667 | 3761 | 4240 | 4304 | 3675 | 3949 | 4092.963 | 4111.9593 | 3675
Fuel rate | kWh/ltr | 3.9366 | 3.8464 | 3.9629 | 4.1724 | 4.0021 | 3.767 | 3.8498 | 4.0103 | 3.8641 | 3.8875 | 3.988 | 3.9696 | 3.9395
Note on H3: feleti ka wolfgramm: 1993380

## 2007
TOWER POWER LTD GENERATIONS FOR YEAR 2007
TONGA POWER: TONGATAPU 2007 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4037888 | 3895636 | 4009831 | 3838703 | 4139750 | 3927478 | 3636760 | 3895094 | 4038522 | 4262203 | 4046032 | 4308081 | 48035978
Power retained by licence | kWh | 95527 | 83649 | 67176 | 77444 | 95468 | 172963 | 86756 | 93184 | 84932 | 104113 | 114299 | 125893 | 1201404
Power supplied to customers | kWh | 3942361 | 3811987 | 3942655 | 3761259 | 4044282 | 3754515 | 3550004 | 3801910 | 3953590 | 4158090 | 3931733 | 4182188 | 46834574
Billing | kWh | 3340241.72 | 3011829.71 | 3574090 | 3015323.52 | 3307287.78 | 3235881.3 | 3010075.08 | 3325345 | 3020651.38 | 3403754 | 3569805.2 | 3647218.06 | 39461502.75
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 602119.28 | 800157.29 | 368565 | 745935.48 | 736994.22 | 518633.7 | 539928.92 | 476565 | 932938.62 | 754336 | 361927.8 | 534969.94 | 7373071.25
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680
Derated capacity | kW | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046
Fuel consumed in generation | litre | 996784 | 967277 | 1013550 | 950485 | 1009345 | 955830 | 928122 | 914772 | 973048 | 1034857 | 987250 | 1040362 | 11771682
Lubricating oil used | litre | 2990.352 | 2901.831 | 3040.65 | 2851.455 | 3028.035 | 2867.49 | 2784.366 | 2744.316 | 2919.144 | 3104.571 | 2961.75 | 3121.086 | 35315.046
Number of consumer | number | 15239 | 15224 | 15213 | 15237 | 15269 | 15242 | 15249 | 15248 | 15264 | 15298 | 15333 | 15355 | 15355
Station running time to generate | hr | 3407.5004 | 3287.4565 | 3383.8236 | 3239.4118 | 3493.4599 | 3314.3274 | 3068.9958 | 3286.9992 | 3408.0354 | 3596.7958 | 3414.373 | 3635.5114 | 40536.6903
Peak demand | kW | 8004.1667 | 7989.6667 | 7981.1667 | 7896.5 | 7821 | 7821 | 7918.9167 | 7904.7083 | 7890.5486 | 7875.4456 | 7871.9365 | 7880.426 | 8004.1667
Minimum demand | kW | 4079.9213 | 3527.3154 | 2900.2496 | 3764.4538 | 3612.3975 | 3130.838 | 3646.4837 | 3697.9324 | 3054.503 | 3368.3706 | 3459.5662 | 3408.6511 | 2900.2496
Fuel rate | kWh/ltr | 4.0509 | 4.0274 | 3.9562 | 4.0387 | 4.1014 | 4.109 | 3.9184 | 4.258 | 4.1504 | 4.1186 | 4.0983 | 4.1409 | 4.0806
Load factor | %
|  | 996784 | 967277 | 1013550 | 950485 | 1009345 | 955830 | 928122 | 914772 | 973048 | 1034857 | 987250 | 1040362
TONGA POWER : VAVA'U 2007 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 473976 | 437036 | 474232 | 436290 | 478206 | 454699 | 446891 | 469017 | 455757 | 469653 | 453369 | 467074 | 5516200
Power retained by licence | kWh | 22556 | 19966 | 21852 | 20950 | 22346 | 21789 | 21581 | 21987 | 30527 | 22613 | 20399 | 10074 | 256640
Power supplied to customers | kWh | 451420 | 417070 | 452380 | 415340 | 455860 | 432910 | 425310 | 447030 | 425230 | 447040 | 432970 | 457000 | 5259560
Billing | kWh | 433869 | 350977 | 356741 | 382246 | 353361 | 392330 | 369876 | 374570 | 369200 | 348848 | 391662 | 356310 | 4479990
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 17551 | 66093 | 95639 | 33094 | 102499 | 40580 | 55434 | 72460 | 56030 | 98192 | 41308 | 100690 | 779570
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272
Derated capacity | kW | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4
Fuel consumed in generation | litre | 121543 | 121544 | 130576 | 120822 | 139525 | 133952 | 130311 | 135558 | 127413 | 132767 | 129076 | 122966 | 1546053
Lubricating oil used | litre | 418.9493 | 438.411 | 451.1585 | 506.0143 | 607.442 | 491.1302 | 426.0783 | 493.4235 | 492.8472 | 550.2089 | 434.5015 | 509.1803 | 5819.345
Number of consumer | number | 3207 | 3210 | 3210 | 3211 | 3215 | 3216 | 3218 | 3216 | 3220 | 3224 | 3224 | 3224 | 3224
Station running time to generate | hr | 2549.3936 | 2343.1117 | 2513.482 | 2362.4237 | 2536.2567 | 2390.3308 | 2245.8131 | 2975.8904 | 5495.3425 | 4088.838 | 4474.0646 | 4913.3353 | 38888.2824
Peak demand | kW | 1042.3577 | 1046.2217 | 964.9281 | 953.982 | 1056.5057 | 1083.6858 | 1010.7152 | 1022.136 | 1045.6558 | 1050.43 | 1092.052 | 1116.6204 | 1116.6204
Minimum demand | kW | 1146697.7225 | 1150948.4571 | 1061517.3868 | 1049475.5858 | 1162261.964 | 1192162.7318 | 1111887.7864 | 1124451.766 | 1150325.9718 | 1155578.039 | 1201366.3883 | 1228394.1215 | 1049475.5858
Fuel rate | kWh/ltr | 3.8997 | 3.5957 | 3.6318 | 3.611 | 3.4274 | 3.3945 | 3.4294 | 3.4599 | 3.577 | 3.5374 | 3.5124 | 3.7984 | 3.5679
TONGA POWER : HA'APAI 2007 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 132080 | 126621 | 143972 | 135434 | 135539 | 132200 | 134264 | 131813 | 130727 | 136615 | 128201 | 135610 | 1603076
Power retained by licence | kWh | 5900 | 5217 | 6320 | 5810 | 4307 | 5348 | 6176 | 5549 | 4655 | 6163 | 5285 | 5782 | 66512
Power supplied to customers | kWh | 126180 | 121404 | 137652 | 129624 | 131232 | 126852 | 128088 | 126264 | 126072 | 130452 | 122916 | 129828 | 1536564
Billing | kWh | 107789 | 108151 | 125900 | 112681 | 118809 | 114010 | 123240 | 108255 | 103865 | 116350 | 115148 | 112690 | 1366888
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 18391 | 13253 | 11752 | 16943 | 12423 | 12842 | 4848 | 18009 | 22207 | 14102 | 7768 | 17138 | 169676
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
Derated capacity | kW | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4
Fuel consumed in generation | litre | 36798 | 35027 | 38880 | 36699 | 37788 | 36129 | 36289 | 36051 | 36228 | 38028 | 36236 | 37517 | 441670
Lubricating oil used | litre | 194.6283 | 266.3884 | 241.6255 | 189.7674 | 236.5748 | 270.4172 | 212.4028 | 182.5898 | 253.6872 | 473.5298 | 167.2047 | 260.5259 | 2949.3418
Number of consumer | number | 989 | 991 | 990 | 991 | 989 | 980 | 981 | 986 | 983 | 977 | 980 | 982 | 991
Station running time to generate | hr | [12 empty] | 0
Peak demand | kW | 304.6888 | 305.138 | 305.4516 | 305.0062 | 304.1481 | 303.3889 | 305 | 307.8333 | 307.3333 | 302.3333 | 299 | 298.8333 | 307.8333
Minimum demand | kW | [12 empty] | 0
Fuel rate | kWh/ltr | 3.5893 | 3.615 | 3.703 | 3.6904 | 3.5868 | 3.6591 | 3.6999 | 3.6563 | 3.6085 | 3.5925 | 3.5379 | 3.6146 | 3.6296
TONGA POWER: 'EUA 2007 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 95405 | 98806 | 109319 | 106108 | 119387 | 109355 | 110897 | 104800 | 103878 | 105997 | 102765 | 112375 | 1279092
Power retained by licence | kWh | 4001 | 13462 | 12143 | 13360 | 11843 | 13907 | 12653 | 9148 | 12594 | 13009 | 12285 | 12667 | 141072
Power supplied to customers | kWh | 91404 | 85344 | 97176 | 92748 | 107544 | 95448 | 98244 | 95652 | 91284 | 92988 | 90480 | 99708 | 1138020
Billing | kWh | 78234 | 75658 | 87255 | 79543 | 94142 | 85186 | 89134 | 85911 | 76638 | 82910 | 86371 | 85191 | 1006173
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 13170 | 9686 | 9921 | 13205 | 13402 | 10262 | 9110 | 9741 | 14646 | 10078 | 4109 | 14517 | 131847
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187
Derated capacity | kW | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
Fuel consumed in generation | litre | 27394 | 25131 | 29561 | 28214 | 32570 | 29746 | 30201 | 30077 | 29639 | 31216 | 29616 | 32618 | 355983
Lubricating oil used | litre | 197.6961 | 206.4277 | 164.0226 | 180.3293 | 202.8946 | 182.8813 | 198.8768 | 197.0766 | 210.5991 | 184.2921 | 190.7211 | 208.3049 | 2324.122
Number of consumer | number | 1072 | 1068 | 1068 | 1066 | 1069 | 1068 | 1079 | 1081 | 1082 | 1087 | 1087 | 1089 | 1089
Station running time to generate | hr | [12 empty] | 0
Peak demand | kW | 280.4459 | 280.5012 | 280.3106 | 280.2662 | 280.3472 | 280.4167 | 280.8333 | 280.8333 | 279.1667 | 280 | 280.8333 | 280.8333 | 280.8333
Minimum demand | kW | [12 empty] | 0
Fuel rate | kWh/ltr | 3.4827 | 3.9316 | 3.6981 | 3.7608 | 3.6656 | 3.6763 | 3.672 | 3.4844 | 3.5048 | 3.3956 | 3.4699 | 3.4452 | 3.5931
TONGA POWER : TONGA 2007 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4739349 | 4558099 | 4737354 | 4516535 | 4872882 | 4623732 | 4328812 | 4600724 | 4728884 | 4974468 | 4730367 | 5023140 | 56434346
Power retained by licence | kWh | 127984 | 122294 | 107491 | 117564 | 133964 | 214007 | 127166 | 129868 | 132708 | 145898 | 152268 | 154416 | 1665628
Power supplied to customers | kWh | 4611365 | 4435805 | 4629863 | 4398971 | 4738918 | 4409725 | 4201646 | 4470856 | 4596176 | 4828570 | 4578099 | 4868724 | 54768718
Billing | kWh | 3960133.72 | 3546615.71 | 4143986 | 3589793.52 | 3873599.78 | 3827407.3 | 3592325.08 | 3894081 | 3570354.38 | 3951862 | 4162986.2 | 4201409.06 | 46314553.75
Transmission losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution losses | kWh | 651231.28 | 889189.29 | 485877 | 809177.48 | 865318.22 | 582317.7 | 609320.92 | 576775 | 1025821.62 | 876708 | 415112.8 | 667314.94 | 8454164.25
Unmetered read | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installed capacity | kW | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511
Derated capacity | kW | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8
Fuel consumed in generation | litre | 1182519 | 1148979 | 1212567 | 1136220 | 1219228 | 1155657 | 1124923 | 1116458 | 1166328 | 1236868 | 1182178 | 1233463 | 14115388
Lubricating oil used | litre | 3801.6257 | 3813.0581 | 3897.4566 | 3727.566 | 4074.9465 | 3811.9186 | 3621.7239 | 3617.4059 | 3876.2775 | 4312.6018 | 3754.1773 | 4099.0971 | 46407.8548
Number of consumer | number | 20507 | 20493 | 20481 | 20505 | 20542 | 20506 | 20527 | 20531 | 20549 | 20586 | 20624 | 20650 | 20659
Station running time to generate | hr | 5956.8941 | 5630.5682 | 5897.3057 | 5601.8356 | 6029.7166 | 5704.6583 | 5314.8089 | 6262.8895 | 8903.3779 | 7685.6337 | 7888.4376 | 8548.8467 | 79424.9727
Peak demand | kW | 9631.6591 | 9621.5276 | 9531.857 | 9435.7544 | 9462.0011 | 9488.4913 | 9515.4652 | 9515.511 | 9522.7044 | 9508.2089 | 9543.8219 | 9576.713 | 9631.6591
Minimum demand | kW | 1150777.6437 | 1154475.7724 | 1064417.6364 | 1053240.0396 | 1165874.3615 | 1195293.5699 | 1115534.27 | 1128149.6984 | 1153380.4748 | 1158946.4097 | 1204825.9545 | 1231802.7726 | 1053240.0396
Fuel rate | kWh/ltr | 4.0078 | 3.9671 | 3.9069 | 3.9751 | 3.9967 | 4.001 | 3.8481 | 4.1208 | 4.0545 | 4.0218 | 4.0014 | 4.0724 | 3.9981
Note on B13: feleti ka wolfgramm: Updated data

## 2008
TOWER POWER LTD GENERATIONS FOR YEAR 2008
TONGA POWER: TONGATAPU 2008 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4334248 | 4263694 | 4403129 | 4385466 | 4036783 | 3892946 | 3879204 | 4074075 | 3704813 | 3920271 | 4046076 | 4014071 | 48954776
Power retained by licence | kWh | 123286 | 124816 | 126311 | 151504 | 164762 | 123216 | 98503 | 140814 | 122464 | 123296 | 125536 | 117286 | 1541794
Power supplied to customers | kWh | 4210962 | 4138878 | 4276818 | 4233962 | 3872021 | 3769730 | 3780701 | 3933261 | 3582349 | 3796975 | 3920540 | 3896785 | 47412982
Billing | kWh | 3456465.81 | 3810412 | 3333635.82 | 3502125.23 | 3401571.78 | 3134271.47 | 3517249 | 3001809 | 3087106.14 | 3284993 | 2898634 | 3723975 | 40152248.25
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 754496.19 | 328466 | 943182.18 | 731836.77 | 470449.22 | 635458.53 | 263452 | 931452 | 495242.86 | 511982 | 1021906 | 172810 | 7260733.75
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680
Derated capacity | kW | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046
Fuel consumed in generation | litre | 1058569 | 1043076 | 1073646 | 1079063 | 984148 | 949734 | 924765 | 998195 | 918029 | 960276 | 998757 | 990144 | 11978402
Lubricating oil used | litre | 3175.707 | 3129.228 | 3220.938 | 3237.189 | 2952.444 | 2849.202 | 2774.295 | 2994.585 | 2754.087 | 2880.828 | 2996.271 | 2970.432 | 35935.206
Number of consumer | number | 15280 | 15244 | 15248 | 15291 | 15309 | 15342 | 15376 | 15376 | 15379 | 15379 | 15339 | 15277 | 15379
Station running time to generate | hr | 3871 | 3491 | 3674 | 3565 | 3221 | 3166 | 2996 | 3210 | 2925 | 3076 | 3154 | 3156 | 39505
Peak demand | kW | 8182 | 8253 | 8312 | 8249 | 8035 | 7807 | 8072 | 8016 | 7579 | 7578 | 7766 | 7680 | 8312
Minimum demand | kW | 3969 | 4104 | 4005 | 3953 | 3097 | 3709 | 3177 | 3772 | 3580 | 3558 | 3770 | 3626 | 3097
Fuel rate | kWh/ltr | 4.0944 | 4.0876 | 4.1011 | 4.0641 | 4.1018 | 4.099 | 4.1948 | 4.0814 | 4.0356 | 4.0824 | 4.0511 | 4.054 | 4.0869
TONGA POWER : VAVA'U 2008 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 467744 | 436374 | 442060 | 431890 | 459389 | 420937 | 412677 | 460325 | 405401 | 436228 | 405303 | 435641 | 5213969
Power retained by licence | kWh | 31134 | 20594 | 20560 | 20320 | 22289 | 20957 | 20847 | 21375 | 18281 | 20078 | 18813 | 41221 | 276469
Power supplied to customers | kWh | 436610 | 415780 | 421500 | 411570 | 437100 | 399980 | 391830 | 438950 | 387120 | 416150 | 386490 | 394420 | 4937500
Billing | kWh | 393558 | 351702 | 344881 | 348957 | 396412 | 332063 | 349035 | 376137 | 342327 | 355555 | 319817 | 345620 | 4256064
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 43052 | 64078 | 76619 | 62613 | 40688 | 67917 | 42795 | 62813 | 44793 | 60595 | 66673 | 48800 | 681436 | 751 | 62.5833
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272
Derated capacity | kW | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4
Fuel consumed in generation | litre | 130162 | 124954 | 126733 | 122350 | 128247 | 116655 | 116172 | 127634 | 111827 | 120912 | 112053 | 117393 | 1455092
Lubricating oil used | litre | 520.648 | 499.816 | 506.932 | 489.4 | 512.988 | 466.62 | 464.688 | 510.536 | 447.308 | 483.648 | 448.212 | 469.572 | 5820.368
Number of consumer | number | 3226 | 3215 | 3214 | 3226 | 3212 | 3220 | 3213 | 3213 | 3226 | 3210 | 3211 | 3217 | 3226
Station running time to generate | hr | 2565 | 2218 | 2177 | 2615 | 2497 | 2427 | 2264 | 2585 | 2144 | 2592 | 2354 | 2182 | 28620
Peak demand | kW | 1082 | 1082 | 1008 | 1010 | 1015 | 1019 | 1002 | 1012 | 979 | 989 | 915 | 875 | 1082
Minimum demand | kW | 480 | 480 | 278 | 474 | 472 | 476 | 382 | 370 | 428 | 425 | 426 | 425 | 278
Fuel rate | kWh/ltr | 3.5936 | 3.4923 | 3.4881 | 3.53 | 3.5821 | 3.6084 | 3.5523 | 3.6066 | 3.6253 | 3.6078 | 3.6171 | 3.711 | 3.5833
TONGA POWER : HA'APAI 2008 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 136068 | 127725 | 135074 | 124896 | 118599 | 116283 | 114468 | 126240 | 108624 | 112567 | 110184 | 119514 | 1450242
Power retained by licence | kWh | 4680 | 5397 | 4694 | 997 | 1611 | 1611 | 420 | 5347 | 5936 | 2215 | 732 | 700 | 34340
Power supplied to customers | kWh | 131388 | 122328 | 130380 | 123899 | 116988 | 114672 | 114048 | 120893 | 102688 | 110352 | 109452 | 118814 | 1415902
Billing | kWh | 114580 | 99820 | 116212 | 110103 | 112127 | 105177 | 97921 | 114851 | 97064 | 98432 | 107084 | 92411 | 1265782
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 16808 | 22508 | 14168 | 13796 | 4861 | 9495 | 16127 | 6042 | 5624 | 11920 | 2368 | 26403 | 150120
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
Derated capacity | kW | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4
Fuel consumed in generation | litre | 38555 | 35430 | 35651 | 37383 | 36014 | 34009 | 35067 | 35901 | 34620 | 34770 | 33254 | 35857 | 426511
Lubricating oil used | litre | 200.5048 | 268.711 | 226.6922 | 175.0018 | 207.0071 | 237.8587 | 181.086 | 174.87 | 210.7944 | 390.1755 | 143.7063 | 229.6032 | 2646.011
Number of consumer | number | 973 | 978 | 992 | 993 | 997 | 997 | 1004 | 1004 | 1005 | 1006 | 1008 | 1009 | 1009
Station running time to generate | hr | 724 | 1326 | 1363 | 829 | 748 | 746 | 784 | 750 | 747 | 726 | 718 | 739 | 10200
Peak demand | kW | 326 | 300 | 298 | 312 | 300 | 315 | 305 | 317 | 295 | 282 | 280 | 314 | 326
Minimum demand | kW | 130 | 108 | 130 | 129 | 129 | 130 | 105 | 109 | 115 | 112 | 118 | 118 | 105
Fuel rate | kWh/ltr | 3.5292 | 3.605 | 3.7888 | 3.341 | 3.2931 | 3.4192 | 3.2643 | 3.5163 | 3.1376 | 3.2375 | 3.3134 | 3.3331 | 3.4002
TONGA POWER: 'EUA 2008 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 109853 | 99064 | 105929 | 94504 | 99675 | 93133 | 95278 | 99156 | 89011 | 89385 | 89126 | 98600 | 1162714
Power retained by licence | kWh | 12761 | 11752 | 10925 | 8572 | 10455 | 10981 | 12802 | 13368 | 4039 | 2037 | 3110 | 2960 | 103762
Power supplied to customers | kWh | 97092 | 87312 | 95004 | 85932 | 89220 | 82152 | 82476 | 85788 | 84972 | 87348 | 86016 | 95640 | 1058952
Billing | kWh | 82937 | 80301 | 81366 | 71340 | 78645 | 69480 | 78052 | 66631 | 65666 | 77366 | 62971 | 79418 | 894173
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 14155 | 7011 | 13638 | 14592 | 10575 | 12672 | 4424 | 19157 | 19306 | 9982 | 23045 | 16222 | 164779 | 61 | 7 | 5.0833 | 0.58333
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187
Derated capacity | kW | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
Fuel consumed in generation | litre | 31832 | 28252 | 30294 | 26209 | 28135 | 24659 | 28887 | 30711 | 23031 | 24375 | 22749 | 27109 | 326243
Lubricating oil used | litre | 238.489 | 216.9011 | 176.4164 | 164.3971 | 174.2645 | 160.6646 | 191.6996 | 221.5887 | 166.6699 | 147.8467 | 150.4212 | 181.1716 | 2190.5303
Number of consumer | number | 1089 | 1095 | 1095 | 1095 | 1097 | 1097 | 1097 | 1098 | 1065 | 1047 | 1050 | 1051 | 1098
Station running time to generate | hr | 1057 | 899 | 945 | 886 | 930 | 893 | 947 | 894 | 913 | 882 | 869 | 965 | 11080
Peak demand | kW | 310 | 280 | 285 | 280 | 280 | 280 | 280 | 280 | 275 | 285 | 285 | 280 | 310
Minimum demand | kW | 115 | 120 | 120 | 120 | 120 | 115 | 112 | 115 | 98 | 95 | 107 | 120 | 95
Fuel rate | kWh/ltr | 3.451 | 3.5064 | 3.4967 | 3.6058 | 3.5427 | 3.7768 | 3.2983 | 3.2287 | 3.8648 | 3.6671 | 3.9178 | 3.6372 | 3.564
TONGA POWER : TONGA 2008 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 5047913 | 4926857 | 5086192 | 5036756 | 4714446 | 4523299 | 4501627 | 4759796 | 4307849 | 4558451 | 4650689 | 4667826 | 56781701
Power retained by licence | kWh | 171861 | 162559 | 162490 | 181393 | 199117 | 156765 | 132572 | 180904 | 150720 | 147626 | 148191 | 162167 | 1956365
Power supplied to customers | kWh | 4876052 | 4764298 | 4923702 | 4855363 | 4515329 | 4366534 | 4369055 | 4578892 | 4157129 | 4410825 | 4502498 | 4505659 | 54825336
Billing | kWh | 4047540.81 | 4342235 | 3876094.82 | 4032525.23 | 3988755.78 | 3640991.47 | 4042257 | 3559428 | 3592163.14 | 3816346 | 3388506 | 4241424 | 46568267.25
Transmission losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution losses | kWh | 828511.19 | 422063 | 1047607.18 | 822837.77 | 526573.22 | 725542.53 | 326798 | 1019464 | 564965.86 | 594479 | 1113992 | 264235 | 8257068.75
Unmetered read | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installed capacity | kW | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511
Derated capacity | kW | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8
Fuel consumed in generation | litre | 1259118 | 1231712 | 1266324 | 1265005 | 1176544 | 1125057 | 1104891 | 1192441 | 1087507 | 1140333 | 1166813 | 1170503 | 14186248
Lubricating oil used | litre | 4135.3488 | 4114.656 | 4130.9785 | 4065.9879 | 3846.7036 | 3714.3453 | 3611.7686 | 3901.5797 | 3578.8593 | 3902.4982 | 3738.6105 | 3850.7789 | 46592.1153
Number of consumer | number | 20568 | 20532 | 20549 | 20605 | 20615 | 20656 | 20690 | 20691 | 20675 | 20642 | 20608 | 20554 | 20712
Station running time to generate | hr | 8217 | 7934 | 8159 | 7895 | 7396 | 7232 | 6991 | 7439 | 6729 | 7276 | 7095 | 7042 | 89405
Peak demand | kW | 9900 | 9915 | 9903 | 9851 | 9630 | 9421 | 9659 | 9625 | 9128 | 9134 | 9246 | 9149 | 9915
Minimum demand | kW | 4694 | 4812 | 4533 | 4676 | 3818 | 4430 | 3776 | 4366 | 4221 | 4190 | 4421 | 4289 | 3776
Fuel rate | kWh/ltr | 4.0091 | 4 | 4.0165 | 3.9816 | 4.007 | 4.0205 | 4.0743 | 3.9916 | 3.9612 | 3.9975 | 3.9858 | 3.9879 | 4.0026

## 2009
TOWER POWER LTD GENERATIONS FOR YEAR 2009
TONGA POWER: TONGATAPU 2009 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4268966 | 3983317 | 4360845 | 3631531 | 3885111 | 3396807 | 3667979 | 3573095 | 3493604 | 3565825 | 3528811 | 3857683 | 45213574
Power retained by licence | kWh | 138114 | 112496 | 112892 | 50397 | 49966 | 39588 | 41803 | 41519 | 38936 | 47799 | 119432 | 129573 | 922515
Power supplied to customers | kWh | 4130852 | 3870821 | 4247953 | 3581134 | 3835145 | 3357219 | 3626176 | 3531576 | 3454668 | 3518026 | 3409379 | 3728110 | 44291059
Billing | kWh | 3297654 | 3221130 | 3467749 | 2980623 | 2972679 | 2933906 | 3078341 | 2660667 | 3014737 | 2993540 | 2855214 | 3491964 | 36968204
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 833198 | 649691 | 780204 | 600511 | 862466 | 423313 | 547835 | 870909 | 439931 | 524486 | 554165 | 236146 | 7322855
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680
Derated capacity | kW | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046
Fuel consumed in generation | litre | 1062867 | 981386 | 1065310 | 893196 | 951385 | 835557 | 900528 | 889460 | 855577 | 909499 | 855455 | 931870 | 11132090
Lubricating oil used | litre | 3188.601 | 2944.158 | 3195.93 | 2679.588 | 2854.155 | 2506.671 | 2701.584 | 2668.38 | 2566.731 | 2728.497 | 2566.365 | 2795.61 | 33396.27
Number of consumer | number | 15230 | 14892 | 14953 | 14970 | 15050 | 15089 | 15140 | 15220 | 15237 | 15266 | 15282 | 15120.8182 | 15282
Station running time to generate | hr | 3653 | 3096 | 3426 | 3009 | 3114 | 2893 | 2992 | 2889 | 2959 | 3412 | 2682 | 2895 | 37020
Peak demand | kW | 7798 | 8059 | 8150 | 7643 | 7479 | 7490 | 7362 | 7362 | 7589 | 6726 | 7255 | 7241 | 8150
Minimum demand | kW | 3429 | 4126 | 4095 | 2796 | 2937 | 2942 | 2888 | 2888 | 3158 | 3305 | 3299 | 3997 | 2796
Fuel rate | kWh/ltr | 4.0165 | 4.0589 | 4.0935 | 4.0658 | 4.0836 | 4.0653 | 4.0731 | 4.0172 | 4.0833 | 3.9206 | 4.1251 | 4.1397 | 4.0616
TONGA POWER: VAVA'U 2009 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 386802 | 409998 | 423573 | 393965 | 417710 | 387516 | 417977 | 423183 | 410744 | 413738 | 403621 | 427228 | 4916055
Power retained by licence | kWh | 17982 | 21788 | 20303 | 19015 | 19730 | 18296 | 19087 | 20173 | 19004 | 19308 | 19091 | 20418 | 234195
Power supplied to customers | kWh | 368820 | 388210 | 403270 | 374950 | 397980 | 369220 | 398890 | 403010 | 391740 | 394430 | 384530 | 406810 | 4681860
Billing | kWh | 325395 | 314819 | 333032 | 311434 | 348079 | 328664 | 385508 | 318276 | 319710 | 358706 | 311454 | 310757 | 3965834
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 43425 | 73391 | 70238 | 63516 | 49901 | 40556 | 13382 | 84734 | 72030 | 35724 | 73076 | 96053 | 716026 | 749 | 62.4167
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272
Derated capacity | kW | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4 | 1208.4
Fuel consumed in generation | litre | 113670 | 105427 | 115363 | 107921 | 125005 | 110279 | 114606 | 116131 | 111185 | 113366 | 110307 | 118628 | 1361888
Lubricating oil used | litre | 454.68 | 421.708 | 461.452 | 431.684 | 500.02 | 441.116 | 458.424 | 464.524 | 444.74 | 453.464 | 441.228 | 474.512 | 5447.552
Number of consumer | number | 3208 | 3220 | 3190 | 3200 | 3200 | 3204 | 3208 | 3209 | 3214 | 3217 | 3220 | 3224 | 3224
Station running time to generate | hr | 2197 | 2048 | 2257 | 2252 | 2383 | 2404 | 2391 | 2484 | 2259 | 2350 | 2290 | 2382 | 27697
Peak demand | kW | 868 | 870 | 892 | 895 | 903 | 892 | 928 | 1010 | 989 | 992 | 996 | 1052 | 1052
Minimum demand | kW | 418 | 415 | 418 | 416 | 396 | 396 | 402 | 418 | 420 | 425 | 428 | 422 | 396
Fuel rate | kWh/ltr | 3.4029 | 3.8889 | 3.6717 | 3.6505 | 3.3415 | 3.514 | 3.6471 | 3.644 | 3.6942 | 3.6496 | 3.6591 | 3.6014 | 3.6097
TONGA POWER: HA'APAI 2009 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 114859 | 109124 | 124817 | 113663 | 130410 | 113212 | 119116 | 117656 | 114944 | 120031 | 114188 | 118064 | 1410084
Power retained by licence | kWh | 2011 | 2024 | 2873 | 3647 | 2754 | 3160 | 3772 | 5216 | 5552 | 4651 | 4208 | 4364 | 44232
Power supplied to customers | kWh | 112848 | 107100 | 121944 | 110016 | 127656 | 110052 | 115344 | 112440 | 109392 | 115380 | 109980 | 113700 | 1365852
Billing | kWh | 119962 | 87166 | 95612 | 102658 | 97010 | 108711 | 97166 | 108781 | 98862 | 105227 | 95362 | 95920 | 1212437
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | -7114 | 19934 | 26332 | 7358 | 30646 | 1341 | 18178 | 3659 | 10530 | 10153 | 14618 | 17780 | 153415
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
Derated capacity | kW | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4
Fuel consumed in generation | litre | 35252 | 32800 | 36437 | 32905 | 36439 | 30975 | 32982 | 30999 | 28979 | 31038 | 30476 | 31026 | 390308
Lubricating oil used | litre | 183.3276 | 248.7643 | 231.6901 | 154.0388 | 209.45 | 216.6389 | 170.319 | 150.9928 | 176.4475 | 348.2964 | 131.7012 | 198.6689 | 2420.3357
Number of consumer | number | 1009 | 1011 | 1011 | 1005 | 1005 | 999 | 1001 | 999 | 999 | 1004 | 1006 | 1006 | 1011
Station running time to generate | hr | 768 | 704 | 745 | 708 | 1368 | 1234 | 1230 | 1056 | 1010 | 1082 | 1036 | 917 | 11858
Peak demand | kW | 289 | 282 | 296 | 312 | 310 | 286 | 293 | 295 | 296 | 290 | 285 | 285 | 312
Minimum demand | kW | 115 | 132 | 130 | 130 | 122 | 119 | 129 | 107 | 109 | 115 | 120 | 104 | 104
Fuel rate | kWh/ltr | 3.2582 | 3.327 | 3.4256 | 3.4543 | 3.5789 | 3.6549 | 3.6115 | 3.7955 | 3.9665 | 3.8672 | 3.7468 | 3.8053 | 3.6127
TONGA POWER: 'EUA 2009 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 97842 | 88419 | 97628 | 91080 | 98142 | 87006 | 90300 | 91900 | 86300 | 87408 | 84238 | 91390 | 1091653
Power retained by licence | kWh | 1998 | 2907 | 1940 | 3276 | 3210 | 1470 | 1980 | 2296 | 2336 | 4044 | 3622 | 3226 | 32305
Power supplied to customers | kWh | 95844 | 85512 | 95688 | 87804 | 94932 | 85536 | 88320 | 89604 | 83964 | 83364 | 80616 | 88164 | 1059348
Billing | kWh | 75780 | 83098 | 76353 | 70869 | 81204 | 65000 | 82223 | 64923 | 67535 | 69180 | 84521 | 77729 | 898415
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 20064 | 2414 | 19335 | 16935 | 13728 | 20536 | 6097 | 24681 | 16429 | 14184 | -3905 | 10435 | 160933
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187
Derated capacity | kW | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
Fuel consumed in generation | litre | 27706 | 24984 | 26603.3 | 24408 | 26553 | 23915 | 25838 | 25340 | 23401 | 25300 | 23836 | 26661 | 304545.3
Lubricating oil used | litre | 207.5765 | 191.8114 | 154.9237 | 153.1002 | 164.4658 | 155.8171 | 171.4659 | 182.8354 | 169.3475 | 153.4573 | 157.6087 | 178.1776 | 2040.5871
Number of consumer | number | 1055 | 1056 | 1060 | 1062 | 1062 | 1063 | 1063 | 1064 | 1064 | 1064 | 1064 | 1065 | 1065
Station running time to generate | hr | 908 | 811 | 918 | 877 | 933 | 865 | 897 | 954 | 864 | 934 | 783 | 1034 | 10778
Peak demand | kW | 285 | 275 | 270 | 280 | 275 | 270 | 270 | 270 | 252 | 260 | 258 | 275 | 285
Minimum demand | kW | 115 | 95 | 110 | 106 | 98 | 89 | 98 | 98 | 85 | 75 | 98 | 118 | 75
Fuel rate | kWh/ltr | 3.5314 | 3.539 | 3.6698 | 3.7316 | 3.6961 | 3.6381 | 3.4949 | 3.6267 | 3.6879 | 3.4549 | 3.5341 | 3.4279 | 3.5845
TONGA POWER: TONGA 2009 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4868469 | 4590858 | 5006863 | 4230239 | 4531373 | 3984541 | 4295372 | 4205834 | 4105592 | 4187002 | 4130858 | 4494365 | 52631366
Power retained by licence | kWh | 160105 | 139215 | 138008 | 76335 | 75660 | 62514 | 66642 | 69204 | 65828 | 75802 | 146353 | 157581 | 1233247
Power supplied to customers | kWh | 4708364 | 4451643 | 4868855 | 4153904 | 4455713 | 3922027 | 4228730 | 4136630 | 4039764 | 4111200 | 3984505 | 4336784 | 51398119
Billing | kWh | 3818791 | 3706213 | 3972746 | 3465584 | 3498972 | 3436281 | 3643238 | 3152647 | 3500844 | 3526653 | 3346551 | 3976370 | 43044890
Transmission losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution losses | kWh | 889573 | 745430 | 896109 | 688320 | 956741 | 485746 | 585492 | 983983 | 538920 | 584547 | 637954 | 360414 | 8353229
Unmetered read | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installed capacity | kW | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511 | 14511
Derated capacity | kW | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8 | 13766.8
Fuel consumed in generation | litre | 1239495 | 1144597 | 1243713.3 | 1058430 | 1139382 | 1000726 | 1073954 | 1061930 | 1019142 | 1079203 | 1020074 | 1108185 | 13188831.3
Lubricating oil used | litre | 4034.1851 | 3806.4417 | 4043.9957 | 3418.4111 | 3728.0908 | 3320.243 | 3501.7929 | 3466.7322 | 3357.266 | 3683.7148 | 3296.9029 | 3646.9685 | 43304.7448
Number of consumer | number | 20502 | 20179 | 20214 | 20237 | 20317 | 20355 | 20412 | 20492 | 20514 | 20551 | 20572 | 20415.8182 | 20582 | 16053.96
Station running time to generate | hr | 7526 | 6659 | 7346 | 6846 | 7798 | 7396 | 7510 | 7383 | 7092 | 7778 | 6791 | 7228 | 87353
Peak demand | kW | 9240 | 9486 | 9608 | 9130 | 8967 | 8938 | 8853 | 8937 | 9126 | 8268 | 8794 | 8853 | 9608
Minimum demand | kW | 4077 | 4768 | 4753 | 3448 | 3553 | 3546 | 3517 | 3511 | 3772 | 3920 | 3945 | 4641 | 3448
Fuel rate | kWh/ltr | 3.9278 | 4.0109 | 4.0257 | 3.9967 | 3.977 | 3.9817 | 3.9996 | 3.9606 | 4.0285 | 3.8797 | 4.0496 | 4.0556 | 3.9906
Lubricant per litre | kWh/ltr | 1206.8036 | 1206.076 | 1238.098 | 1237.4869 | 1215.4674 | 1200.0751 | 1226.6208 | 1213.1984 | 1222.8975 | 1136.6249 | 1252.9511 | 1232.3564 | 1215.3718

## 2010
TOWER POWER LTD GENERATIONS FOR YEAR 2010
TONGA POWER: TONGATAPU 2010 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4131364 | 3408861 | 3886532 | 3825922 | 3861173 | 3719277 | 3670139 | 3695793 | 3648033 | 3777618 | 3640895 | 3921814 | 45187421
Power retained by licence | kWh | 132269 | 97908 | 55537 | 95162 | 131026 | 124585 | 125377 | 114763 | 108147 | 120766 | 107854 | 125510 | 1338904
Power supplied to customers | kWh | 3999095 | 3310953 | 3830995 | 3730760 | 3730147 | 3594692 | 3544762 | 3581030 | 3539886 | 3656852 | 3533041 | 3796304 | 43848517
Billing | kWh | 3046453 | 2820845 | 3565004 | 3006937 | 2984294 | 3051303 | 3153486 | 2893787 | 2968589 | 3034457 | 2983832 | 3769912 | 37278899
Transmission losses | kWh
Distribution losses | kWh | 952642 | 490108 | 265991 | 723823 | 745853 | 543389 | 391276 | 687243 | 571297 | 622395 | 549209 | 26392 | 6569618
Unmetered read | kWh
Installed capacity | kW | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680 | 12680
Derated capacity | kW | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046 | 12046
Fuel consumed in generation | litre | 1007503 | 841062 | 1003699 | 925994 | 937261 | 896474 | 877334 | 904139 | 889991 | 920756 | 883291 | 996497 | 11084001
Lubricating oil used | litre | 3022.509 | 2523.186 | 3011.097 | 2777.982 | 3344 | 5492 | 3428 | 5041 | 3030.69 | 3710 | 4161 | 4497 | 44038.464
Number of consumer | number | 15339 | 15358 | 15378 | 15407 | 15433 | 15453 | 15490 | 15534 | 15566 | 15604 | 15566 | 15514 | 15604
Station running time to generate | hr | 3181 | 2962 | 3906 | 2976 | 2962 | 2816 | 2798 | 3032 | 2961 | 3051 | 2886 | 3248 | 36779
Peak demand | kW | 7298 | 7365 | 7279 | 7285 | 7360 | 7040 | 6781 | 7213 | 7277 | 7248 | 7315 | 7697 | 7697
Minimum demand | kW | 3937 | 3545 | 3980 | 3756 | 3527 | 3863 | 3645 | 3670 | 3461 | 3495 | 3070 | 3811 | 3070
Fuel rate | kWh/ltr | 4.1006 | 4.053 | 3.8722 | 4.1317 | 4.1196 | 4.1488 | 4.1833 | 4.0876 | 4.099 | 4.1027 | 4.122 | 3.9356 | 4.0768
TONGA POWER: VAVA'U 2010 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 441031 | 308713 | 414079 | 392722 | 396344 | 403046 | 432465 | 430127 | 423154 | 426885 | 387153 | 414029 | 4869748
Power retained by licence | kWh | 21371 | 16883 | 21019 | 20152 | 13832 | 19961 | 20863 | 20173 | 19502 | 4720 | 4257 | 4520 | 187253
Power supplied to customers | kWh | 419660 | 291830 | 393060 | 372570 | 382512 | 383085 | 411602 | 409954 | 403652 | 422165 | 382896 | 409509 | 4682495
Billing | kWh | 321968 | 256285 | 342075 | 347147 | 309729 | 318927 | 373397 | 328972 | 329600 | 369465 | 323079 | 376673 | 3997317
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 97692 | 35545 | 50985 | 25423 | 72783 | 64158 | 38205 | 80982 | 74052 | 52700 | 59817 | 32836 | 685178
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872
Derated capacity | kW | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4
Fuel consumed in generation | litre | 122047 | 84723 | 114499 | 109964 | 125223 | 104523 | 110998 | 110253 | 108188 | 111320 | 101401 | 110358 | 1313497
Lubricating oil used | litre | 488.188 | 338.892 | 457.996 | 439.856 | 1220 | 417 | 550 | 668 | 569 | 613 | 697 | 739 | 7197.932
Number of consumer | number | 3226 | 3230 | 3238 | 3239 | 3239 | 3243 | 3241 | 3165 | 3166 | 3170 | 3166 | 3188 | 3243
Station running time to generate | hr | 2691 | 1611 | 2577 | 2358 | 1132 | 1475 | 1591 | 1606 | 1549 | 1561 | 1403 | 1510 | 21064
Peak demand | kW | 1052 | 885 | 887 | 896 | 898 | 902 | 910 | 905 | 915 | 921 | 923 | 934 | 1052
Minimum demand | kW | 422 | 268 | 418 | 412 | 410 | 402 | 406 | 404 | 408 | 412 | 405 | 408 | 268
Fuel rate | kWh/ltr | 3.6136 | 3.6438 | 3.6164 | 3.5714 | 3.1651 | 3.8561 | 3.8962 | 3.9013 | 3.9113 | 3.8348 | 3.818 | 3.7517 | 3.7075
TONGA POWER: HA'APAI 2010 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 125708 | 94233 | 126521 | 120483 | 127827 | 121858 | 125071 | 123903 | 121757 | 129837 | 121594 | 122361 | 1461153
Power retained by licence | kWh | 5084 | 3453 | 5021 | 4875 | 5787 | 5578 | 4171 | 5283 | 4613 | 5145 | 4906 | 2025 | 55941
Power supplied to customers | kWh | 120624 | 90780 | 121500 | 115608 | 122040 | 116280 | 120900 | 118620 | 117144 | 124692 | 116688 | 120336 | 1405212
Billing | kWh | 96157 | 81331 | 123476 | 92200 | 100462 | 102171 | 111291 | 98874 | 113622 | 99200 | 103156 | 116580 | 1238520
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 24467 | 9449 | -1976 | 23408 | 21578 | 14109 | 9609 | 19746 | 3522 | 25492 | 13532 | 3756 | 166692
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
Derated capacity | kW | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4
Fuel consumed in generation | litre | 34641 | 26198 | 34349 | 33208 | 33343 | 32202 | 34029 | 32348 | 33167 | 34775 | 32889 | 34101 | 395250
Lubricating oil used | litre | 180.1501 | 198.6929 | 218.4132 | 155.4573 | 216 | 164 | 153 | 195 | 176 | 179 | 224 | 156 | 2215.7136
Number of consumer | number | 1010 | 1010 | 1012 | 1012 | 1013 | 1016 | 1017 | 967 | 967 | 973 | 967 | 979 | 1017
Station running time to generate | hr | 1089 | 1141 | 1274 | 1123 | 1277 | 1189.9 | 1180.3 | 1183.9 | 1175.3 | 1321.2 | 1230.4 | 1187 | 14372
Peak demand | kW | 285 | 270 | 270 | 278 | 278 | 285 | 287 | 285 | 298 | 295 | 282 | 281 | 298
Minimum demand | kW | 109 | 102 | 102 | 115 | 115 | 118 | 120 | 118 | 124 | 128 | 111 | 115 | 102
Fuel rate | kWh/ltr | 3.6289 | 3.597 | 3.6834 | 3.6281 | 3.8337 | 3.7842 | 3.6754 | 3.8303 | 3.671 | 3.7336 | 3.6971 | 3.5882 | 3.6968
TONGA POWER: 'EUA 2010 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 95784 | 70483 | 90385 | 89647 | 90455 | 83800 | 89272 | 90924 | 85463 | 91745 | 88944 | 97037 | 1063939
Power retained by licence | kWh | 3768 | 2779 | 4105 | 3691 | -7741 | 2596 | 772 | 3444 | 3299 | 3077 | 3842 | 3161 | 26793
Power supplied to customers | kWh | 92016 | 67704 | 86280 | 85956 | 98196 | 81204 | 88500 | 87480 | 82164 | 88668 | 85102 | 93876 | 1037146
Billing | kWh | 67797 | 55421 | 71931 | 72432 | 65334 | 65545 | 73783 | 67657 | 66977 | 69975 | 69974 | 79614 | 826440
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 24219 | 12283 | 14349 | 13524 | 32862 | 15659 | 14717 | 19823 | 15187 | 18693 | 15128 | 14262 | 210706
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187
Derated capacity | kW | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
Fuel consumed in generation | litre | 26993 | 18960 | 24329 | 24098 | 27400 | 21940 | 24050 | 24380 | 23509 | 25654 | 24584 | 27643 | 293540
Lubricating oil used | litre | 202.2346 | 145.5629 | 141.6793 | 151.1557 | 200 | 200 | 150 | 160 | 160 | 350 | 180 | 200 | 2240.6326
Number of consumer | number | 1071 | 1071 | 1071 | 1071 | 1073 | 1073 | 1073 | 1020 | 1021 | 1024 | 1022 | 1025 | 1073
Station running time to generate | hr | 928 | 754 | 869 | 1252 | 713 | 696 | 891 | 891 | 860 | 917 | 892 | 945 | 10608
Peak demand | kW | 275 | 265 | 270 | 270 | 270 | 270 | 265 | 275 | 265 | 275 | 275 | 275 | 275
Minimum demand | kW | 98 | 28 | 98 | 100 | 68 | 96 | 83 | 100 | 88 | 100 | 112 | 128 | 28
Fuel rate | kWh/ltr | 3.5485 | 3.7175 | 3.7151 | 3.7201 | 3.3013 | 3.8195 | 3.7119 | 3.7295 | 3.6353 | 3.5762 | 3.618 | 3.5104 | 3.6245
0.0072351
TONGA POWER: TONGA 2010 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4793887 | 3882290 | 4517517 | 4428774 | 4475799 | 4327981 | 4316947 | 4340747 | 4278407 | 4426085 | 4238586 | 4555241 | 52582261
Power retained by licence | kWh | 162492 | 121023 | 85682 | 123880 | 142904 | 152720 | 151183 | 143663 | 135561 | 133708 | 120859 | 135216 | 1608891
Power supplied to customers | kWh | 4631395 | 3761267 | 4431835 | 4304894 | 4332895 | 4175261 | 4165764 | 4197084 | 4142846 | 4292377 | 4117727 | 4420025 | 50973370
Billing | kWh | 3532375 | 3213882 | 4102486 | 3518716 | 3459819 | 3537946 | 3711957 | 3389290 | 3478788 | 3573097 | 3480041 | 4342779 | 43341176
Transmission losses | kWh | [12 empty] | 0
Distribution losses | kWh | 1099020 | 547385 | 329349 | 786178 | 873076 | 637315 | 453807 | 807794 | 664058 | 719280 | 637686 | 77246 | 7632194
Unmetered read | kWh | [12 empty] | 0
Installed capacity | kW | 15111 | 15111 | 15111 | 15111 | 15111 | 15111 | 15111 | 15111 | 15111 | 15111 | 15111 | 15111 | 15111
Derated capacity | kW | 14336.8 | 14336.8 | 14336.8 | 14336.8 | 14336.8 | 14336.8 | 14336.8 | 14336.8 | 14336.8 | 14336.8 | 14336.8 | 14336.8 | 14336.8
Fuel consumed in generation | litre | 1191184 | 970943 | 1176876 | 1093264 | 1123227 | 1055139 | 1046411 | 1071120 | 1054855 | 1092505 | 1042165 | 1168599 | 13086288
Lubricating oil used | litre | 3893.0818 | 3206.3339 | 3829.1856 | 3524.451 | 4980 | 6273 | 4281 | 6064 | 3935.69 | 4852 | 5262 | 5592 | 55692.7422
Number of consumer | number | 20646 | 20669 | 20699 | 20729 | 20758 | 20785 | 20821 | 20686 | 20720 | 20771 | 20721 | 20706 | 20937
Station running time to generate | hr | 7889 | 6468 | 8626 | 7709 | 6084 | 6176.9 | 6460.3 | 6712.9 | 6545.3 | 6850.2 | 6411.4 | 6890 | 82823
Peak demand | kW | 8910 | 8785 | 8706 | 8729 | 8806 | 8497 | 8243 | 8678 | 8755 | 8739 | 8795 | 9187 | 9187
Minimum demand | kW | 4566 | 3943 | 4598 | 4383 | 4120 | 4479 | 4254 | 4292 | 4081 | 4135 | 3698 | 4462 | 3698
Fuel rate | kWh/ltr | 4.0245 | 3.9985 | 3.8386 | 4.051 | 3.9848 | 4.1018 | 4.1255 | 4.0525 | 4.0559 | 4.0513 | 4.0671 | 3.898 | 4.0181
Lubricant per kWh | kWh/ltr | 1231.3862 | 1210.819 | 1179.7592 | 1256.5855 | 898.7548 | 689.938 | 1008.3969 | 715.8224 | 1087.0793 | 912.2187 | 805.5086 | 814.5996 | 944.1493

## 2011
TOWER POWER LTD GENERATIONS FOR YEAR 2011
TONGA POWER: TONGATAPU 2011 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4377459 | 3304168 | 4151518 | 3915016 | 3833492 | 3706703 | 3637951 | 3587169 | 3407892 | 3742854 | 3744898 | 3988923 | 45398043
Power retained by licence | kWh | 127034 | 96021 | 110220 | 113125 | 62599 | 108640 | 112423 | 96215 | 106785 | 112039 | 109756 | 113197 | 1268054
Power supplied to customers | kWh | 4250425 | 3208147 | 4041298 | 3801891 | 3770893 | 3598063 | 3525528 | 3490954 | 3301107 | 3630815 | 3635142 | 3875726 | 44129989
Billing | kWh | 3089558 | 3114817 | 3700524 | 3314569 | 3112242 | 3184439 | 3046335 | 2953144 | 2908890 | 3019566 | 3228899 | 3673286 | 38346269 | 37881676 | 464593
Distribution losses | kWh | 1160867 | 93330 | 340774 | 487322 | 658651 | 413624 | 479193 | 537810 | 392217 | 611249 | 406243 | 202440 | 5783720
Installed capacity | kW | 11280 | 11280 | 11280 | 11280 | 11280 | 11280 | 11280 | 11280 | 11280 | 11280 | 11280 | 11280 | 11280
Derated capacity | kW | 10716 | 10716 | 10716 | 10716 | 10716 | 10716 | 10716 | 10716 | 10716 | 10716 | 10716 | 10716 | 10716
Fuel consumed in generation | litre | 1082890 | 817389 | 1028246.2542 | 969864.5202 | 962240.7586 | 906005.3624 | 887160.741 | 878420.6757 | 829983 | 916850 | 915961.457 | 976884.15 | 11171895.9191
Lubricating oil used | litre | 2844 | 4663 | 2889 | 5734 | 9719 | 4005 | 4176.2 | 1788 | 5883 | 2104 | 3303 | 3981 | 51089.2
Number of consumer | number | 15612 | 15612 | 15483 | 15484 | 15559 | 15597 | 15608 | 15599 | 15521 | 15356 | 15384 | 15369 | 15612
Station running time to generate | hr | 3516 | 2644 | 3392 | 3244 | 3699 | 3048 | 3021 | 2981 | 2746 | 2920 | 3047 | 3275 | 37533
Peak demand | kW | 7359 | 7429 | 7619 | 7688 | 7283 | 7457 | 7133 | 7249 | 7145 | 7145 | 7145 | 7145 | 7688
Minimum demand | kW | 3031 | 3696 | 3367 | 3723 | 3462 | 3433 | 3208 | 3324 | 3683 | 3683 | 3683 | 3683 | 3031
Fuel rate | kWh/ltr | 4.0424 | 4.0423 | 4.0375 | 4.0367 | 3.9839 | 4.0913 | 4.1007 | 4.0837 | 4.106 | 4.0823 | 4.0885 | 4.0833 | 4.0636
TONGA POWER: VAVA'U 2011 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 410881.6 | 364808.2 | 422559.7 | 407494 | 443139.8 | 394208.4 | 401427 | 409235.6 | 400668 | 422147 | 395188.4 | 427934.6 | 4899692.3
Power retained by licence | kWh | 6240 | 5592 | 8640 | 7200 | 7280 | 4880 | 3920 | 6240 | 6560 | 6320 | 7040 | 7120 | 77032
Power supplied to customers | kWh | 404641.6 | 359216.2 | 413919.7 | 400294 | 435859.8 | 389328.4 | 397507 | 402995.6 | 394108 | 415827 | 388148.4 | 420814.6 | 4822660.3
Billing | kWh | 313628 | 309443 | 349628 | 364426 | 367834 | 337418 | 349541 | 335435 | 363043 | 347043 | 342642 | 390001 | 4170082
Distribution losses | kWh | 91013.6 | 49773.2 | 64291.7 | 35868 | 68025.8 | 51910.4 | 47966 | 67560.6 | 31065 | 68784 | 45506.4 | 30813.6 | 652578.3
Installed capacity | kW | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872 | 1872
Derated capacity | kW | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4
Fuel consumed in generation | litre | 107674 | 95987.361 | 110254 | 105668 | 115610 | 102916 | 104810.7323 | 106681.5089 | 106769.1172 | 111926.5604 | 103337.7824 | 117287.119 | 1288922.1812
Lubricating oil used | litre | 665 | 570 | 595 | 588 | 685 | 497 | 665 | 543 | 531 | 563 | 447 | 553 | 6902
Number of consumer | number | 3165 | 3165 | 3204 | 3205 | 3211 | 3218 | 3171 | 3146 | 3155 | 3158 | 3165 | 3163 | 3218
Station running time to generate | hr | 1575.5 | 1394.3 | 1454.7 | 1345 | 1532 | 1829 | 1377.1 | 1462.5 | 1761.5 | 1859.5 | 1679.9 | 1660 | 18931
Peak demand | kW | 922 | 918 | 920 | 906 | 1090 | 915 | 910 | 922 | 1000 | 988 | 895 | 966 | 1090
Minimum demand | kW | 410 | 415 | 413 | 418 | 416 | 402 | 408 | 411 | 382 | 398 | 390 | 418 | 382
Fuel rate | kWh/ltr | 3.816 | 3.8006 | 3.8326 | 3.8564 | 3.833 | 3.8304 | 3.83 | 3.836 | 3.7527 | 3.7716 | 3.8242 | 3.6486 | 3.8014
TONGA POWER: HA'APAI 2011 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 112453 | 106539 | 125323 | 119600 | 122258 | 115028 | 119431 | 120021 | 112547 | 117064 | 110625 | 117340 | 1398229
Power retained by licence | kWh | 1813 | 1779 | 2071 | 1856 | 1766 | 1736 | 1855 | 2037 | 1655 | 1804 | 1761 | 1756 | 21889
Power supplied to customers | kWh | 110640 | 104760 | 123252 | 117744 | 120492 | 113292 | 117576 | 117984 | 110892 | 115260 | 108864 | 115584 | 1376340
Billing | kWh | 89994 | 90887 | 123476 | 92200 | 102858 | 108965 | 97536 | 100687 | 103977 | 94849 | 94886 | 119045 | 1219360
Distribution losses | kWh | 20646 | 13873 | -224 | 25544 | 17634 | 4327 | 20040 | 17297 | 6915 | 20411 | 13978 | -3461 | 156980
Installed capacity | kW | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
Derated capacity | kW | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4
Fuel consumed in generation | litre | 29623 | 28029.5643 | 34349 | 33208 | 34189.6081 | 32113.7192 | 32476.4359 | 32541.0282 | 30756 | 31519 | 29781.3675 | 32283.8583 | 380870.5814
Lubricating oil used | litre | 178 | 167 | 152 | 210 | 162 | 154 | 194 | 540 | 124 | 172 | 154 | 215 | 2422
Number of consumer | number | 993 | 993 | 985 | 988 | 989 | 992 | 993 | 974 | 976 | 978 | 981 | 970 | 993
Station running time to generate | hr | 1089 | 1141 | 1274 | 1123 | 1277 | 1126.9 | 1120.6 | 1140.7 | 976.6 | 1099.8 | 1025 | 1096.9 | 13490.5
Peak demand | kW | 285 | 270 | 270 | 278 | 278 | 285 | 287 | 285 | 298 | 295 | 273 | 290 | 298
Minimum demand | kW | 109 | 102 | 102 | 115 | 115 | 118 | 120 | 118 | 124 | 128 | 109 | 108 | 102
Fuel rate | kWh/ltr | 3.7961 | 3.801 | 3.6485 | 3.6015 | 3.5759 | 3.5819 | 3.6775 | 3.6883 | 3.6594 | 3.7141 | 3.7146 | 3.6346 | 3.6711
TONGA POWER: 'EUA 2011 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 96230 | 86109 | 95414 | 94515 | 98428 | 100210 | 103449 | 96058 | 92614 | 92627 | 89698 | 104976 | 1150328
Power retained by licence | kWh | 2810 | 2133 | 2522 | 2271 | 2668 | 2374 | 3489 | 2254 | 2386 | 1883 | 2890 | 2184 | 29864
Power supplied to customers | kWh | 93420 | 83976 | 92892 | 92244 | 95760 | 97836 | 99960 | 93804 | 90228 | 90744 | 86808 | 102792 | 1120464
Billing | kWh | 68250 | 62270 | 68971 | 73609 | 71362 | 77063 | 81326 | 74544 | 70155 | 81077 | 76917 | 89494 | 895038
Distribution losses | kWh | 25170 | 21706 | 23921 | 18635 | 24398 | 20773 | 18634 | 19260 | 20073 | 9667 | 9891 | 13298 | 225426
Installed capacity | kW | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187
Derated capacity | kW | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
Fuel consumed in generation | litre | 24918 | 22699 | 24886 | 27673 | 25800 | 29100 | 28474 | 27060.3038 | 25543 | 25506 | 24434.6962 | 28140 | 314234
Lubricating oil used | litre | 200 | 160 | 160 | 200 | 120 | 160 | 200 | 160 | 376 | 80 | 80 | 96 | 1992
Number of consumer | number | 1042 | 1042 | 1031 | 1032 | 1038 | 1039 | 1042 | 1029 | 1031 | 1032 | 1032 | 1034 | 1042
Station running time to generate | hr | 903 | 803.6 | 920.5 | 876.9 | 967.4 | 924.9 | 970 | 1003.6 | 903.8 | 899.1 | 856.2 | 945 | 10974
Peak demand | kW | 280 | 270 | 275 | 270 | 275 | 285 | 270 | 270 | 275 | 270 | 275 | 280 | 285
Minimum demand | kW | 49 | 88 | 78 | 109 | 110 | 110 | 115 | 98 | 98 | 110 | 92 | 120 | 49
Fuel rate | kWh/ltr | 3.8619 | 3.7935 | 3.834 | 3.4154 | 3.815 | 3.4436 | 3.6331 | 3.5498 | 3.6258 | 3.6316 | 3.6709 | 3.7305 | 3.6607
TONGA POWER: TONGA 2011 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4997023.6 | 3861624.2 | 4794814.7 | 4536625 | 4497317.8 | 4316149.4 | 4262258 | 4212483.6 | 4013721 | 4374692 | 4340409.4 | 4639173.6 | 52846292.3
Power retained by licence | kWh | 137897 | 105525 | 123453 | 124452 | 74313 | 117630 | 121687 | 106746 | 117386 | 122046 | 121447 | 124257 | 1396839
Power supplied to customers | kWh | 4859126.6 | 3756099.2 | 4671361.7 | 4412173 | 4423004.8 | 4198519.4 | 4140571 | 4105737.6 | 3896335 | 4252646 | 4218962.4 | 4514916.6 | 51449453.3
Billing | kWh | 3561430 | 3577417 | 4242599 | 3844804 | 3654296 | 3707885 | 3574738 | 3463810 | 3446065 | 3542535 | 3743344 | 4271826 | 44630749
Distribution losses | kWh | 1297696.6 | 178682.2 | 428762.7 | 567369 | 768708.8 | 490634.4 | 565833 | 641927.6 | 450270 | 710111 | 475618.4 | 243090.6 | 6818704.3
Installed capacity | kW | 13711 | 13711 | 13711 | 13711 | 13711 | 13711 | 13711 | 13711 | 13711 | 13711 | 13711 | 13711 | 13711
Derated capacity | kW | 13006.8 | 13006.8 | 13006.8 | 13006.8 | 13006.8 | 13006.8 | 13006.8 | 13006.8 | 13006.8 | 13006.8 | 13006.8 | 13006.8 | 13006.8
Fuel consumed in generation | litre | 1245105 | 964104.9253 | 1197735.2542 | 1136413.5202 | 1137840.3666 | 1070135.0815 | 1052921.9092 | 1044703.5165 | 993051.1172 | 1085801.5604 | 1073515.3031 | 1154595.1273 | 13155922.6817
Lubricating oil used | litre | 3887 | 5560 | 3796 | 6732 | 10686 | 4816 | 5235.2 | 3031 | 6914 | 2919 | 3984 | 4845 | 62405.2
Number of consumer | number | 20812 | 20812 | 20703 | 20709 | 20797 | 20846 | 20814 | 20748 | 20683 | 20524 | 20562 | 20536 | 20865
Station running time to generate | hr | 7083.5 | 5982.9 | 7041.2 | 6588.9 | 7475.4 | 6928.8 | 6488.7 | 6587.8 | 6387.9 | 6778.4 | 6608.1 | 6976.9 | 80928.5
Peak demand | kW | 8846 | 8887 | 9084 | 9142 | 8926 | 8942 | 8600 | 8726 | 8718 | 8698 | 8588 | 8681 | 9142
Minimum demand | kW | 3599 | 4301 | 3960 | 4365 | 4103 | 4063 | 3851 | 3951 | 4287 | 4319 | 4274 | 4329 | 3599
Fuel rate | kWh/ltr | 4.0133 | 4.0054 | 4.0032 | 3.9921 | 3.9525 | 4.0333 | 4.048 | 4.0322 | 4.0418 | 4.029 | 4.0432 | 4.018 | 4.0169
Lubricant per litre | kWh/ltr | 1285.5733 | 694.5367 | 1263.1229 | 673.8896 | 420.8607 | 896.2104 | 814.1538 | 1389.7999 | 580.5208 | 1498.6954 | 1089.4602 | 957.5178 | 846.8251

## 2012
TOWER POWER LTD GENERATIONS FOR YEAR 2012
TONGA POWER: TONGATAPU 2012 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4100835 | 3507091 | 4125412 | 3835524 | 3732940 | 3533301 | 3555351 | 3596221 | 3546110 | 3729916 | 3713643 | 3962549 | 44938893
Power retained by licence | kWh | 94960 | 76424 | 100724 | 98844 | 93159 | 91740 | 84314 | 93887 | 88467 | 89979 | 88016 | 108610 | 1109124
Power supplied to customers | kWh | 4005875 | 3430667 | 4024688 | 3736680 | 3639781 | 3441561 | 3471037 | 3502334 | 3457643 | 3639937 | 3625627 | 3853939 | 43829769
Billing | kWh | 3248520 | 3167295 | 3736983 | 3030152 | 3418272 | 2951851 | 2987703 | 3284554 | 2776492 | 3397072 | 3187003 | 3579144 | 38765041
Distribution losses | kWh | 757355 | 263372 | 287705 | 706528 | 221509 | 489710 | 483334 | 217780 | 681151 | 242865 | 438624 | 274795 | 5064728
Installed capacity | kW | 11280 | 11280 | 11280 | 11280 | 11280 | 11280 | 11280 | 11280 | 12580 | 12580 | 12580 | 12580 | 12580
Derated capacity | kW | 10716 | 10716 | 10716 | 10716 | 10716 | 10716 | 10716 | 10716 | 12016 | 12016 | 12016 | 12016 | 12016
Fuel consumed in generation | litre | 1005878.7582 | 865426.8768 | 1016287.851 | 943300.519 | 911080 | 857600 | 866880 | 848331 | 824629 | 874120 | 868938 | 921930.826 | 10804402.831
Lubricating oil used | litre | 4122 | 5363 | 4275 | 2531 | 3005 | 6143 | 3490 | 4346.48 | 3912.16 | 6071 | 5185 | 3634.47 | 52078.11
Number of consumer | number | 15344 | 15376 | 15404 | 15450 | 15452 | 15354 | 15347 | 15369 | 15333 | 15192 | 15185 | 15229 | 15452
Station running time to generate | hr | 3397 | 2907 | 3294 | 3016 | 3039 | 2775 | 2917 | 2853 | 2760 | 2889 | 2895 | 3033 | 35775
Peak demand | kW | 7400 | 7619 | 7595 | 7586 | 7501 | 7183 | 7307 | 7274 | 7453 | 7499 | 7388 | 7619 | 7619
Minimum demand | kW | 3677 | 3499 | 3779 | 3689 | 3414 | 3383 | 3334 | 3269 | 3339 | 3432 | 3248 | 3518 | 3248
Fuel rate | kWh/ltr | 4.0769 | 4.0524 | 4.0593 | 4.0661 | 4.0973 | 4.12 | 4.1013 | 4.2392 | 4.3002 | 4.2671 | 4.2738 | 4.2981 | 4.1593
TONGA POWER: VAVA'U 2012 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 434607.2 | 368546 | 428688.3 | 403808.9 | 419214 | 397401 | 403192 | 409542 | 402229 | 428787 | 408567 | 427563.3 | 4932145.7
Power retained by licence | kWh | 6880 | 5200 | 6480 | 6240 | 6320 | 6000 | 6160 | 6240 | 6152 | 6408 | 6560 | 7120 | 75760
Power supplied to customers | kWh | 427727.2 | 363346 | 422208.3 | 397568.9 | 412894 | 412894 | 412894 | 412894 | 412894 | 412894 | 412894 | 420443.3 | 4921551.7
Billing | kWh | 352703 | 310139 | 353227 | 308557 | 335074 | 383888 | 352268 | 351411 | 404909 | 340020 | 362612 | 355624 | 4210432
Distribution losses | kWh | 75024.2 | 53207 | 68981.3 | 89011.9 | 77820 | 29006 | 60626 | 61483 | 7985 | 72874 | 50282 | 64819.3 | 711119.7
Installed capacity | kW | 1872 | 1860 | 1860 | 1860 | 1860 | 1860 | 1860 | 1860 | 1860 | 1860 | 1860 | 1860 | 1872
Derated capacity | kW | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4
Fuel consumed in generation | litre | 118901.2984 | 100161.2993 | 116266.8295 | 102643.6066 | 120063 | 100047 | 102558 | 103069 | 101644 | 108429 | 104051 | 108472.1892 | 1286306.223
Lubricating oil used | litre | 514 | 465 | 532 | 509 | 448 | 535 | 527 | 601 | 432 | 550 | 552 | 512.5 | 6177.5
Number of consumer | number | 3177 | 3185 | 3192 | 3164 | 3167 | 3152 | 3159 | 3161 | 3163 | 3167 | 3169 | 3177 | 3192
Station running time to generate | hr | 1499.6 | 1266 | 1378 | 1379 | 1380 | 1381 | 1382 | 1383 | 1384 | 1385 | 1386 | 1387 | 16590.6
Peak demand | kW | 941 | 994 | 1007 | 903 | 902 | 907 | 953 | 942 | 905 | 924 | 912 | 1022 | 1022
Minimum demand | kW | 410 | 23 | 418 | 416 | 410 | 412 | 412 | 398 | 402 | 418 | 411 | 445 | 23
Fuel rate | kWh/ltr | 3.6552 | 3.6795 | 3.6871 | 3.9341 | 3.4916 | 3.9721 | 3.9314 | 3.9735 | 3.9572 | 3.9545 | 3.9266 | 3.9417 | 3.8343
TONGA POWER: HA'APAI 2012 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 119987 | 105853 | 120868 | 116749 | 133430 | 107369 | 112172 | 117919 | 103674 | 120968 | 113850 | 124244 | 1397083
Power retained by licence | kWh | 2003 | 1573 | 2020 | 1573 | 2294 | 1829 | 1904 | 1962 | 1733 | 1930 | 1900 | 2035 | 22756
Power supplied to customers | kWh | 117984 | 104280 | 118848 | 115176 | 131136 | 105540 | 110268 | 115957 | 101941 | 119038 | 111950 | 122209 | 1374327
Billing | kWh | 102881 | 91195 | 111129 | 101736 | 128531 | 81709 | 96936 | 114620 | 96576 | 109487 | 111618 | 104224 | 1250642
Distribution losses | kWh | 15103 | 13085 | 7719 | 13440 | 2605 | 23831 | 13332 | 1337 | 5365 | 9551 | 332 | 17985 | 123685
Installed capacity | kW | 558 | 558 | 558 | 558 | 558 | 558 | 558 | 558 | 558 | 558 | 558 | 558 | 558
Derated capacity | kW | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1
Fuel consumed in generation | litre | 31951.2718 | 29380.133 | 33911.4507 | 32201.1239 | 36075 | 28259 | 29353 | 32376 | 28703 | 31241 | 31731 | 34240.5928 | 379422.5723
Lubricating oil used | litre | 180 | 177 | 237 | 54 | 65 | 170 | 49.5 | 47 | 41 | 52 | 48.5 | 190 | 1311
Number of consumer | number | 974 | 976 | 963 | 966 | 967 | 969 | 973 | 974 | 975 | 965 | 966 | 966 | 976
Station running time to generate | hr | 1240.1 | 967.4 | 1112.6 | 1115.7 | 1417.3 | 987.2 | 1026.9 | 1068.1 | 1120 | 1207 | 1142.2 | 1277.8 | 13682.3
Peak demand | kW | 262 | 247 | 257 | 280 | 293 | 289 | 269 | 275 | 181 | 282 | 281 | 280 | 293
Minimum demand | kW | 109 | 110 | 110 | 109 | 112 | 103 | 105 | 115 | 118 | 118 | 118 | 122 | 103
Fuel rate | kWh/ltr | 3.7553 | 3.6029 | 3.5642 | 3.6256 | 3.6987 | 3.7995 | 3.8215 | 3.6422 | 3.612 | 3.8721 | 3.588 | 3.6286 | 3.6821
TONGA POWER: 'EUA 2012 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 93851 | 86170 | 100155 | 89856 | 95321 | 91753 | 91606 | 94504 | 90635 | 94648 | 89128 | 95715 | 1113342
Power retained by licence | kWh | 2975 | 2338 | 2607 | 2184 | 2309 | 2761 | 2182 | 2236 | 1823 | 1907 | 1718 | 1828 | 26868
Power supplied to customers | kWh | 90876 | 83832 | 97548 | 87672 | 93012 | 88992 | 89424 | 92268 | 88812 | 92741 | 87410 | 93887 | 1086474
Billing | kWh | 76338 | 73035 | 83775 | 73581 | 82214 | 82274 | 73374 | 84779 | 71927 | 79300 | 77855 | 83518 | 941970
Distribution losses | kWh | 14538 | 10797 | 13773 | 14091 | 10798 | 6718 | 16050 | 7489 | 16885 | 13441 | 9555 | 10369 | 144504
Installed capacity | kW | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360
Derated capacity | kW | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342
Fuel consumed in generation | litre | 25443.3038 | 23900 | 27501 | 24300 | 26206 | 25299 | 25304 | 25901 | 24713 | 27139 | 23739 | 26911.6962 | 306357
Lubricating oil used | litre | 100 | 104 | 110 | 158 | 148 | 200 | 164 | 202 | 210 | 250 | 230 | 200 | 2076
Number of consumer | number | 1041 | 1042 | 1022 | 1023 | 1018 | 1023 | 1025 | 1027 | 1029 | 1026 | 1027 | 1030 | 1042
Station running time to generate | hr | 884.3 | 847.7 | 937.1 | 883.6 | 912.1 | 893.5 | 923.5 | 928.2 | 886 | 916 | 893 | 786 | 10691
Peak demand | kW | 270 | 270 | 270 | 270 | 275 | 270 | 270 | 270 | 270 | 270 | 270 | 275 | 275
Minimum demand | kW | 105 | 98 | 128 | 96 | 110 | 116 | 118 | 110 | 110 | 11 | 110 | 110 | 11
Fuel rate | kWh/ltr | 3.6886 | 3.6054 | 3.6419 | 3.6978 | 3.6374 | 3.6267 | 3.6202 | 3.6487 | 3.6675 | 3.4875 | 3.7545 | 3.5566 | 3.6341
TONGA POWER: TONGA 2012 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Gross Generation | kWh | 4749280.2 | 4067660 | 4775123.3 | 4445937.9 | 4380905 | 4129824 | 4162321 | 4218186 | 4142648 | 4374319 | 4325188 | 4610071.3 | 52381463.7
Power retained by licence | kWh | 106818 | 85535 | 111831 | 108841 | 104082 | 102330 | 94560 | 104325 | 98175 | 100224 | 98194 | 119593 | 1234508
Power supplied to customers | kWh | 4642462.2 | 3982125 | 4663292.3 | 4337096.9 | 4276823 | 4048987 | 4083623 | 4123453 | 4061290 | 4264610 | 4237881 | 4490478.3 | 51212121.7
Billing | kWh | 3780442 | 3641664 | 4285114 | 3514026 | 3964091 | 3499722 | 3510281 | 3835364 | 3349904 | 3925879 | 3739088 | 4122510 | 45168085
Distribution losses | kWh | 862020.2 | 340461 | 378178.3 | 823070.9 | 312732 | 549265 | 573342 | 288089 | 711386 | 338731 | 498793 | 367968.3 | 6044036.7
Installed capacity | kW | 14070 | 14058 | 14058 | 14058 | 14058 | 14058 | 14058 | 14058 | 15358 | 15358 | 15358 | 15358 | 15358
Derated capacity | kW | 13366.5 | 13366.5 | 13366.5 | 13366.5 | 13366.5 | 13366.5 | 13366.5 | 13366.5 | 14666.5 | 14666.5 | 14666.5 | 14666.5 | 14666.5
Fuel consumed in generation | litre | 1182174.6323 | 1018868.3091 | 1193967.1312 | 1102445.2495 | 1093424 | 1011205 | 1024095 | 1009677 | 979689 | 1040929 | 1028459 | 1091555.3042 | 12776488.6263
Lubricating oil used | litre | 4916 | 6109 | 5154 | 3252 | 3666 | 7048 | 4230.5 | 5196.48 | 4595.16 | 6923 | 6015.5 | 4536.97 | 61642.61
Number of consumer | number | 20536 | 20579 | 20581 | 20603 | 20604 | 20498 | 20504 | 20531 | 20500 | 20350 | 20347 | 20402 | 20662 | 16116.36
Station running time to generate | hr | 7021 | 5988.1 | 6721.7 | 6394.3 | 6748.4 | 6036.7 | 6249.4 | 6232.3 | 6150 | 6397 | 6316.2 | 6483.8 | 76738.9
Peak demand | kW | 8873 | 9130 | 9129 | 9039 | 8971 | 8649 | 8799 | 8761 | 8809 | 8975 | 8851 | 9196 | 9196
Minimum demand | kW | 4301 | 3730 | 4435 | 4310 | 4046 | 4014 | 3969 | 3892 | 3969 | 3979 | 3887 | 4195 | 3730
Fuel rate | kWh/ltr | 4.0174 | 3.9923 | 3.9994 | 4.0328 | 4.0066 | 4.0841 | 4.0644 | 4.1778 | 4.2285 | 4.2023 | 4.2055 | 4.2234 | 4.0998
lubricant per kWh | kWh/ltr | 966.0863 | 665.8471 | 926.4888 | 1367.1396 | 1195.0095 | 585.9569 | 983.8839 | 811.7391 | 901.5242 | 631.8531 | 719.0072 | 1016.1124 | 849.7606

## 2013
TOWER POWER LTD GENERATIONS FOR YEAR 2013
TONGA POWER: TONGATAPU 2013 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Power Generated | kWh | 4136142 | 3814125 | 4170236 | 3825551 | 3945004 | 3805378 | 3780074 | 3842846 | 3468374 | 3731091 | 3985097 | 4215611 | 46719529
Power generated by Diesel | kWh | 3934179 | 3650263 | 4009776 | 3636825 | 3789644 | 3662398 | 3641492 | 3677937 | 3298118 | 3537781 | 3785966 | 4026959 | 44651338
Power Generated by Solar | kWh | 201963 | 163862 | 160460 | 188726 | 155360 | 142980 | 138582 | 164909 | 170256 | 193310 | 199131 | 188652 | 2068191 | 48177
Parasitic Losses | kWh | 108299 | 106626 | 104243 | 57986 | 107183 | 98226 | 100790 | 104070 | 87620 | 98558 | 103577 | 109716 | 1186894
Power Sent Out | kWh | 4027843 | 3707499 | 4065993 | 3767565 | 3837821 | 3707152 | 3679284 | 3738776 | 3380754 | 3632533 | 3881520 | 4105895 | 45532635
Distribution Losses | kWh | 430962 | 476603 | 396461 | 601176 | -70531 | 573488 | 487434 | 443101 | 305733 | 218572 | 185746 | 368067.7273 | 4416812.7273
Billing | kWh | 3596881 | 3230896 | 3669532 | 3166389 | 3908352 | 3133664 | 3191850 | 3295675 | 3075021 | 3413961 | 3695774 | 3737827.2727 | 41115822.2727
Installed capacity | kW | 12580 | 12580 | 12580 | 12580 | 12580 | 12580 | 12580 | 12580 | 12580 | 12580 | 12580 | 12580 | 12580
Derated capacity | kW | 12016 | 12016 | 12016 | 12016 | 12016 | 12016 | 12016 | 12016 | 12016 | 12016 | 12016 | 12016 | 12016
Fuel consumed in generation | litre | 967386.069 | 898886.74 | 1026441.69 | 854332 | 941262 | 887693 | 892110 | 896716 | 804017 | 880717 | 931450 | 1009872 | 10990883.499
Lubricating oil used | litre | 4551.9 | 4411.94 | 4578 | 4838 | 1925 | 4608 | 3746 | 2811 | 357 | 4455 | 3628.184 | 6732 | 46642.024
Number of consumer | number | 15229 | 15256 | 15289 | 15311 | 15345 | 15377 | 15395 | 15399 | 15410 | 15350 | 15392 | 15403 | 15410
Station running time to generate | hr | 3355 | 3044 | 3405 | 3428 | 3010 | 2886 | 2823 | 3028 | 2648 | 2833 | 3046 | 3136 | 36642
Peak demand | kW | 7682 | 7874 | 7823 | 7348 | 7779 | 7849 | 7347 | 7360 | 7502 | 7352 | 7591.6 | 7903 | 7903
Minimum demand | kW | 3766 | 3818 | 3207 | 3677 | 3576 | 3613 | 3093 | 3324 | 3265 | 3380 | 3471.9 | 3398 | 3093
Fuel rate | kWh/ltr | 4.0668 | 4.0609 | 3.9065 | 4.2569 | 4.0261 | 4.1257 | 4.0819 | 4.1016 | 4.1021 | 4.0169 | 4.0646 | 3.9876 | 4.0626
Disconnections | number | 1019 | 1179 | 1218 | 1149 | 1488 | 864 | 1519 | 1080 | 983 | 1303 | 1094 | 1265 | 14161
Reconnections | number | 1053 | 1032 | 1149 | 1028 | 1312 | 1017 | 1290 | 1236 | 899 | 1141 | 1136 | 1146 | 13439
TONGA POWER: VAVA'U 2013 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Power Generated | kWh | 441966 | 380208 | 409794.8 | 397500 | 425832 | 402002 | 405665 | 427697 | 404005 | 413594 | 402899 | 421279 | 4932441.8
Power generated by Diesel | kWh | 441966 | 380208 | 409794.8 | 397500 | 425832 | 402002 | 405665 | 427697 | 404005 | 413594 | 402899 | 421279 | 4932441.8
Power Generated by Solar | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33119 | 73268 | 106387
Parasitic Losses | kWh | 8560 | 7200 | 7200 | 7760 | 7680 | 6960 | 6720 | 7040 | 6880 | 6880 | 8344 | 9017 | 90241
Power Sent Out | kWh | 433406 | 373008 | 402594.8 | 389740 | 418152 | 395042 | 398945 | 420657 | 397125 | 406714 | 394555 | 412262 | 4842200.8
Distribution losses | kWh | 83316 | 58073 | 35610 | 39268 | 27373 | 64309 | 47321 | 36846 | 40211 | 39422 | 48707 | 47314.1818 | 567770.1818
Billing | kWh | 350090 | 314935 | 366985 | 350472 | 390779 | 330733 | 351624 | 383811 | 356914 | 367292 | 345848 | 364947.8182 | 4274430.8182
Installed capacity | kW | 1860 | 1860 | 1860 | 1860 | 1860 | 1860 | 1860 | 1860 | 1860 | 1860 | 2280 | 2280 | 2280
Derated capacity | kW | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 1778.4 | 2198 | 2198 | 2198
Fuel consumed in generation | litre | 112708.1616 | 96547.0906 | 103716.9121 | 101470 | 99938 | 103001 | 103797 | 109414 | 103231 | 106316 | 96694 | 90373 | 1227206.1643
Lubricating oil used | litre | 473 | 313 | 511 | 467 | 425 | 519 | 520 | 403 | 561 | 440 | 463.2 | 549 | 5644.2
Number of consumer | number | 3177 | 3181 | 3188 | 3200 | 3210 | 3190 | 3188 | 3196 | 3201 | 3210 | 3217 | 3224 | 3224
Station running time to generate | hr | 1388 | 1389 | 1390 | 1391 | 1392 | 1393 | 1394 | 1395 | 1396 | 1397 | 1392.5 | 1138 | 16455.5
Peak demand | kW | 951 | 931 | 882 | 904 | 922 | 907 | 929 | 964 | 919 | 920 | 922.9 | 897 | 964
Minimum demand | kW | 448 | 431 | 428 | 406 | 318 | 419 | 403 | 403 | 417 | 413 | 408.6 | 399 | 318
Fuel rate | kWh/ltr | 3.9213 | 3.9381 | 3.9511 | 3.9174 | 4.261 | 3.9029 | 3.9083 | 3.909 | 3.9136 | 3.8902 | 4.1667 | 4.6616 | 4.0192
Disconnections | number | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reconnections | number | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TONGA POWER: HA'APAI 2013 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Power Generated | kWh | 126578 | 114079 | 129044 | 121094 | 127946 | 119815 | 122419 | 124034 | 115506 | 118549 | 117487 | 127339 | 1463890
Power generated by Diesel | kWh | 126578 | 114079 | 129044 | 121094 | 127946 | 119815 | 122419 | 124034 | 115506 | 118549 | 117487 | 127339 | 1463890
Power Generated by Solar | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parasitic Losses | kWh | 2093 | 1893 | 2316 | 1882 | 2012 | 1896 | 1816 | 1666 | 888 | 1827 | 1145 | 2006 | 21440
Power Sent Out | kWh | 124485 | 112186 | 126728 | 119212 | 125934 | 117919 | 120603 | 122368 | 114618 | 116722 | 116342 | 125333 | 1442450
Distribution losses | kWh | 13681 | 10248 | 12704 | 13860 | 1777 | 23951 | 9804 | 9657 | 13890 | 6709 | 9410 | 11426.4545 | 137117.4545
Billing | kWh | 110804 | 101938 | 114024 | 105352 | 124157 | 93968 | 110799 | 112711 | 100728 | 110013 | 106932 | 113906.5455 | 1305332.5455
Installed capacity | kW | 558 | 558 | 558 | 558 | 558 | 558 | 558 | 558 | 558 | 558 | 558 | 558 | 558
Derated capacity | kW | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1 | 530.1
Fuel consumed in generation | litre | 35269.8024 | 30158.7766 | 37419.8024 | 32908 | 35390 | 32137 | 33956 | 33710 | 32483 | 33748 | 31815 | 35386 | 404381.3813
Lubricating oil used | litre | 264 | 178 | 39 | 34 | 29 | 66 | 30 | 27 | 122 | 18 | 80.7 | 35 | 922.7
Number of consumer | number | 966 | 966 | 967 | 967 | 969 | 973 | 975 | 975 | 966 | 969 | 969 | 972 | 975
Station running time to generate | hr | 1353.2 | 1213.4 | 1371.5 | 1267 | 1360 | 1243 | 1229 | 1199 | 728 | 806 | 1177.01 | 1327 | 14274.11
Peak demand | kW | 281 | 268 | 284 | 272 | 285 | 285 | 286 | 300 | 282 | 285 | 282.8 | 286 | 300
Minimum demand | kW | 122 | 128 | 130 | 124 | 114 | 122 | 128 | 121 | 109 | 118 | 121.6 | 118 | 109
Fuel rate | kWh/ltr | 3.5888 | 3.7826 | 3.4485 | 3.6798 | 3.6153 | 3.7283 | 3.6052 | 3.6794 | 3.5559 | 3.5128 | 3.6928 | 3.5986 | 3.6201
number
Disconnections | number | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reconnections | number | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TONGA POWER: 'EUA 2013 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Power Generated | kWh | 96791 | 90406 | 103345 | 90732 | 110886 | 95685 | 95921 | 98208 | 92870 | 91906 | 96240 | 100634 | 1163624
Power generated by Diesel | kWh | 96791 | 90406 | 103345 | 90732 | 110886 | 95685 | 95921 | 98208 | 92870 | 91906 | 96240 | 100634 | 1163624
Power Generated by Solar | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parasitic Losses | kWh | 2860 | 2931 | 1973 | 2800 | 2558 | 2276 | 2296 | 2400 | 2430 | 2564 | 2800 | 2929 | 30817
Power Sent Out | kWh | 93931 | 87475 | 101372 | 87932 | 108328 | 93409 | 93625 | 95808 | 90440 | 89342 | 93440 | 97705 | 1132807
Distribution losses | kWh | 17963 | 14738 | 17536 | 9000 | 16654 | 8193 | 8382 | 6598 | 14320 | 9399 | 7419 | 11836.5455 | 142038.5455
Billing | kWh | 75968 | 72737 | 83836 | 78932 | 91674 | 85216 | 85243 | 89210 | 76120 | 79943 | 86021 | 85868.4545 | 990768.4545
Installed capacity | kW | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360
Derated capacity | kW | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342
Fuel consumed in generation | litre | 26959 | 24223 | 27860 | 24218 | 29615 | 26914 | 26110 | 27010 | 26209 | 25620 | 26525 | 27731 | 318994
Lubricating oil used | litre | 139 | 200 | 149 | 140 | 140 | 146 | 145 | 145 | 146 | 160 | 151 | 142 | 1803
Number of consumer | number | 1030 | 1032 | 1032 | 1029 | 1034 | 1038 | 1038 | 1039 | 1036 | 1036 | 1041 | 1044 | 1044
Station running time to generate | hr | 737 | 808 | 967 | 973 | 1125 | 1035 | 893 | 1055 | 993 | 898 | 948.4 | 928 | 11360.4
Peak demand | kW | 230 | 270 | 275 | 275 | 290 | 280 | 275 | 270 | 270 | 270 | 270.5 | 280 | 290
Minimum demand | kW | 65 | 98 | 118 | 110 | 150 | 118 | 115 | 115 | 118 | 118 | 112.5 | 131 | 65
Fuel rate | kWh/ltr | 3.5903 | 3.7322 | 3.7094 | 3.7465 | 3.7443 | 3.5552 | 3.6737 | 3.636 | 3.5434 | 3.5873 | 3.6283 | 3.6289 | 3.6478
Disconnections | number | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reconnections | number | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TONGA POWER: TONGA 2013 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Power Generated | kWh | 4801477 | 4398818 | 4812419.8 | 4434877 | 4609668 | 4422880 | 4404079 | 4492785 | 4080755 | 4355140 | 4601723 | 4864863 | 54279484.8
Power generated by Diesel | kWh | 4599514 | 4234956 | 4651959.8 | 4246151 | 4454308 | 4279900 | 4265497 | 4327876 | 3910499 | 4161830 | 4402592 | 4676211 | 52211293.8
Power Generated by Solar | kWh | 201963 | 163862 | 160460 | 188726 | 155360 | 142980 | 138582 | 164909 | 170256 | 193310 | 232250 | 261920 | 2174578
Parasitic Losses | kWh | 121812 | 118650 | 115732 | 70428 | 119433 | 109358 | 111622 | 115176 | 97818 | 109829 | 115866 | 123668 | 1329392
Power Sent Out | kWh | 4679665 | 4280168 | 4696687.8 | 4364449 | 4490235 | 4313522 | 4292457 | 4377609 | 3982937 | 4245311 | 4485857 | 4741195 | 52950092.8
Distribution losses | kWh | 545922 | 559662 | 462311 | 663304 | -24727 | 669941 | 552941 | 496202 | 374154 | 274102 | 251282 | 438644.9091 | 5263738.9091
Billing | kWh | 4133743 | 3720506 | 4234377 | 3701145 | 4514962 | 3643581 | 3739516 | 3881407 | 3608783 | 3971209 | 4234575 | 4302550.0909 | 47686354.0909
Installed capacity | kW | 15358 | 15358 | 15358 | 15358 | 15358 | 15358 | 15358 | 15358 | 15358 | 15358 | 15778 | 15778 | 15778
Derated capacity | kW | 14666.5 | 14666.5 | 14666.5 | 14666.5 | 14666.5 | 14666.5 | 14666.5 | 14666.5 | 14666.5 | 14666.5 | 15086.1 | 15086.1 | 15086.1
Fuel consumed in generation | litre | 1142323.033 | 1049815.6072 | 1195438.4045 | 1012928 | 1106205 | 1049745 | 1055973 | 1066850 | 965940 | 1046401 | 1086484 | 1163362 | 12941465.0446
Lubricating oil used | litre | 5427.9 | 5102.94 | 5277 | 5479 | 2519 | 5339 | 4441 | 3386 | 1186 | 5073 | 4323.084 | 7458 | 55011.924
Number of consumer | number | 20402 | 20435 | 20476 | 20507 | 20558 | 20578 | 20596 | 20609 | 20613 | 20565 | 20619 | 20643 | 20643
Station running time to generate | hr | 6833.2 | 6454.4 | 7133.5 | 7059 | 6887 | 6557 | 6339 | 6677 | 5765 | 5934 | 6563.91 | 6529 | 78732.01
Peak demand | kW | 9144 | 9343 | 9264 | 8799 | 9276 | 9321 | 8837 | 8894 | 8973 | 8827 | 9067.8 | 9366 | 9366
Minimum demand | kW | 4401 | 4475 | 3883 | 4317 | 4158 | 4272 | 3739 | 3963 | 3909 | 4029 | 4114.6 | 4046 | 3739
Fuel rate | kWh/ltr | 4.2033 | 4.1901 | 4.0257 | 4.3783 | 4.1671 | 4.2133 | 4.1706 | 4.2113 | 4.2246 | 4.162 | 4.2354 | 4.1817 | 4.1942
Disconnections | number | 1019 | 1179 | 1218 | 1149 | 1488 | 864 | 1519 | 1080 | 983 | 1303 | 1094 | 1265 | 14161
Reconnections | number | 1053 | 1032 | 1149 | 1028 | 1312 | 1017 | 1290 | 1236 | 899 | 1141 | 1136 | 1146 | 13439
Lubricant per litre | kWh/ltr | 847.3837 | 829.9051 | 881.5539 | 774.9865 | 1768.2842 | 801.6295 | 960.4812 | 1278.1677 | 3297.2167 | 820.3883 | 1018.3915 | 627.006 | 949.0905
Load Factor |  | 70.5774 | 70.0617 | 69.822 | 70.0029 | 66.7938 | 63.7778 | 66.985 | 67.8962 | 63.1641 | 66.3157 | 70.4833 | 69.8142 | 66.1573
|  | 70.58% | 70.06% | 69.82% | 70% | 66.79% | 63.78% | 66.98% | 67.9% | 63.16% | 66.32% | 70.48% | 69.81% | 66.16%

## 2014
TOWER POWER LTD GENERATIONS FOR YEAR 2014
TONGA POWER: TONGATAPU 2014 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Power Generated | kWh | January: 4380716; February: 4072188; March: 4262549
Power generated by Diesel | kWh | January: 4182056; February: 3885636; March: 4100653
Power Generated by Solar | kWh | January: 198660; February: 186552; March: 161896
Parasitic Losses | kWh | January: 98382; February: 94059; March: 115480
Power Sent Out | kWh | January: 4282334; February: 3978129; March: 4147069
Distribution Losses | kWh | January: 378031; February: 392134; March: 0
Billing | kWh | January: 3904303; February: 3585995; March: 0
Installed capacity | kW | January: 12591; February: 12591; March: 12591
Derated capacity | kW | January: 12027; February: 12027; March: 12027
Fuel consumed in generation | litre | January: 1039556; February: 967366; March: 1003178
Lubricating oil used | litre | January: 5977; February: 3535; March: 5557
Number of consumer | number | January: 14980; February: 14827; March: 14788
Station running time to generate | hr | January: 3380; February: 3597; March: 3353
Peak demand | kW | January: 7662; February: 8180; March: 8012
Minimum demand | kW | January: 3886; February: 4640; March: 1837
Fuel rate | kWh/ltr | January: 4.02; February: 4.02; March: 4.09
Third Party Solar | kWh | January: 23875; February: 24293; March: 22882
TPL Micro-Solar | kWh | January: 11007; February: 7519; March: 8683
TPL Micro-Wind | kWh | January: 555; February: 226; March: 2161
TONGA POWER: VAVA'U 2014 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Power Generated | kWh | 555 January: 420181; 226 February: 389587; 2161 March: 417901
Power generated by Diesel | kWh | 555 January: 353066; 226 February: 322886; 2161 March: 358066
Power generated by Solar | kWh | 555 January: 67115; 226 February: 66701; 2161 March: 59835
Parasitic Losses | kWh | 555 January: 8349; 226 February: 7333; 2161 March: 9132
Power Sent Out | kWh | 555 January: 411832; 226 February: 382254; 2161 March: 408769
Distribution losses | kWh | 555 January: 96703; 226 February: -9339; 2161 March: 0
Billing | kWh | 555 January: 315129; 226 February: 391593; 2161 March: 0
Installed capacity | kW | 555 January: 2280; 226 February: 2280; 2161 March: 2280
Derated capacity | kW | 555 January: 2198; 226 February: 2198; 2161 March: 2198
Fuel consumed in generation | litre | 555 January: 92346; 226 February: 84945; 2161 March: 93253
Lubricating oil used | litre | 555 January: 303; 226 February: 438; 2161 March: 553
Number of consumer | number | 555 January: 3106; 226 February: 3130; 2161 March: 3128
Station running time to generate | hr | 555 January: 1266; 226 February: 1199; 2161 March: 1229
Peak demand | kW | 555 January: 923; 226 February: 904; 2161 March: 890
Minimum demand | kW | 555 January: 238; 226 February: 441; 2161 March: 370
Fuel rate | kWh/ltr | 555 January: 3.82; 226 February: 3.8; 2161 March: 3.84
TONGA POWER: HA'APAI 2014 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Power Generated | kWh | 3.82 January: 63835; 3.8 February: 83711; 3.84 March: 105577
Power generated by Diesel | kWh | 3.82 January: 63835; 3.8 February: 83711; 3.84 March: 105577
Power generated by Solar | kWh | 3.82 January: 0; 3.8 February: 0; 3.84 March: 0
Parasitic Losses | kWh | 3.82 January: 1710; 3.8 February: 1730; 3.84 March: 2050
Power Sent Out | kWh | 3.82 January: 62125; 3.8 February: 81981; 3.84 March: 103527
Distribution losses | kWh | 3.82 January: 62125; 3.8 February: -44581; 3.84 March: 0
Billing | kWh | 3.82 January: 0; 3.8 February: 126562; 3.84 March: 0
Installed capacity | kW | 3.82 January: 772; 3.8 February: 772; 3.84 March: 772
Derated capacity | kW | 3.82 January: 744; 3.8 February: 744; 3.84 March: 744
Fuel consumed in generation | litre | 3.82 January: 17538; 3.8 February: 22538; 3.84 March: 25821
Lubricating oil used | litre | 3.82 January: 14; 3.8 February: 24; 3.84 March: 30
Number of consumer | number | 3.82 January: 0; 3.8 February: 677; 3.84 March: 725
Station running time to generate | hr | 3.82 January: 783; 3.8 February: 806; 3.84 March: 977
Peak demand | kW | 3.82 January: 269; 3.8 February: 230; 3.84 March: 228
Minimum demand | kW | 3.82 January: 124; 3.8 February: 109; 3.84 March: 129
Fuel rate | kWh/ltr | 3.82 January: 3.64; 3.8 February: 3.71; 3.84 March: 4.09
TONGA POWER: 'EUA 2014 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Power Generated | kWh | 3.64 January: 103670; 3.71 February: 90063; 4.09 March: 100847
Power generated by Diesel | kWh | 3.64 January: 103670; 3.71 February: 90063; 4.09 March: 100847
Power generated by Solar | kWh | 3.64 January: 0; 3.71 February: 0; 4.09 March: 0
Parasitic Losses | kWh | 3.64 January: 2365; 3.71 February: 2038; 4.09 March: 2225
Power Sent Out | kWh | 3.64 January: 101305; 3.71 February: 88025; 4.09 March: 98622
Distribution losses | kWh | 3.64 January: 15033; 3.71 February: 6765; 4.09 March: 0
Billing | kWh | 3.64 January: 86272; 3.71 February: 81260; 4.09 March: 0
Installed capacity | kW | 3.64 January: 372; 3.71 February: 372; 4.09 March: 372
Derated capacity | kW | 3.64 January: 364; 3.71 February: 364; 4.09 March: 364
Fuel consumed in generation | litre | 3.64 January: 28179; 3.71 February: 24516; 4.09 March: 27771
Lubricating oil used | litre | 3.64 January: 0; 3.71 February: 127; 4.09 March: 142
Number of consumer | number | 3.64 January: 1045; 3.71 February: 1014; 4.09 March: 1040
Station running time to generate | hr | 3.64 January: 939; 3.71 February: 816; 4.09 March: 959
Peak demand | kW | 3.64 January: 280; 3.71 February: 275; 4.09 March: 275
Minimum demand | kW | 3.64 January: 115; 3.71 February: 115; 4.09 March: 118
Fuel rate | kWh/ltr | 3.64 January: 3.68; 3.71 February: 3.67; 4.09 March: 3.63
TONGA POWER: TONGA 2014 | Unit | January | February | March | April | May | June | July | August | September | October | November | December | Total
Power Generated | kWh | 3.68 January: 4968402; 3.67 February: 4635549; 3.63 March: 4886874 | 14490825
Power generated by Diesel | kWh | 3.68 January: 4702627; 3.67 February: 4382296; 3.63 March: 4665143 | 13750066
Power generated by Solar | kWh | 3.68 January: 265775; 3.67 February: 253253; 3.63 March: 221731 | 740759
Parasitic Losses | kWh | 3.68 January: 110806; 3.67 February: 105160; 3.63 March: 128887 | 344853
Power Sent Out | kWh | 3.68 January: 4857596; 3.67 February: 4530389; 3.63 March: 4757987 | 14145972
Distribution losses | kWh | 3.68 January: 551892; 3.67 February: 344979; 3.63 March: 0 | 896871
Billing | kWh | 3.68 January: 4305704; 3.67 February: 4185410; 3.63 March: 0 | 8491114
Installed capacity | kW | 3.68 January: 16015; 3.67 February: 16015; 3.63 March: 16015 | 16015
Derated capacity | kW | 3.68 January: 15333; 3.67 February: 15333; 3.63 March: 15333 | 15333
Fuel consumed in generation | litre | 3.68 January: 1177619; 3.67 February: 1099365; 3.63 March: 1150023 | 3427007
Lubricating oil used | litre | 3.68 January: 6294; 3.67 February: 4124; 3.63 March: 6282 | 16700
Number of consumer | number | 3.68 January: 19131; 3.67 February: 19648; 3.63 March: 19681 | 58460
Station running time to generate | hr | 3.68 January: 6368; 3.67 February: 6418; 3.63 March: 6518 | 19304
Peak demand | kW | 3.68 January: 9134; 3.67 February: 9589; 3.63 March: 9405 | 9589
Minimum demand | kW | 3.68 January: 4363; 3.67 February: 5305; 3.63 March: 2454 | 5305
Fuel rate | kWh/ltr | 3.68 January: 3.9933; 3.67 February: 3.9862; 3.63 March: 4.0566 | 4.0123
Lubricant per kWh | kWh/ltr | 3.68 January: 747.1603; 3.67 February: 1062.6324; 3.63 March: 742.6207 | 823.3572

## Generation & fuel used
Year | Month | Tongatapu |  |  | Year | Month | Vava'u |  |  | Year | Month | Ha'apai |  |  | Year | Month | 'Eua |  |  | Year | Month | Total
|  | Generation (mWh) | Net generation (mWh) | Fuel used (kj) |  |  | Generation (mWh) | Net generation (mWh) | Fuel used (kj) |  |  | Generation (mWh) | Net generation (mWh) | Fuel used (kj) |  |  | Generation (mWh) | Net generation (mWh) | Fuel used (kj) |  |  | Generation (mWh) | Net generation (mWh) | Fuel used (kj)
2006 | Jan | 4249.941 | 4197.708 | 1070.657 | 2006 | Jan | 448.804 | 427.84 | 119.074 | 2006 | Jan | 131.428 | 126.096 | 35.189 | 2006 | Jan | 91.691 | 90.756 | 25.36 | 2006 | Jan | 4921.864 | 4842.4 | 1250.28
| Feb | 3484.053 | 3430.747 | 900.847 |  | Feb | 411.462 | 391.87 | 109.655 |  | Feb | 114.791 | 110.868 | 31.117 |  | Feb | 81.37 | 77.076 | 22.143 |  | Feb | 4091.676 | 4010.561 | 1063.762
| Mar | 4477.261 | 4423.955 | 1120.128 |  | Mar | 487.537 | 463.66 | 128.765 |  | Mar | 141.274 | 136.476 | 39.002 |  | Mar | 106.638 | 96.444 | 27.475 |  | Mar | 5212.71 | 5120.535 | 1315.37
| Apr | 4396.89 | 4323.435 | 1033.456 |  | Apr | 455.049 | 435.63 | 121.787 |  | Apr | 135.624 | 130.956 | 37.169 |  | Apr | 94.146 | 91.656 | 25.508 |  | Apr | 5081.709 | 4981.677 | 1217.92
| May | 3989.057 | 3935.661 | 982.5141 |  | May | 446.293 | 425.43 | 121.039 |  | May | 155.411 | 149.772 | 41.232 |  | May | 94.147 | 91.824 | 25.832 |  | May | 4684.908 | 4602.687 | 1170.6171
| Jun | 3714.904 | 3657.578 | 998.611 |  | Jun | 438.467 | 418.43 | 116.885 |  | Jun | 179.053 | 126.372 | 35.459 |  | Jun | 95.673 | 87.42 | 24.557 |  | Jun | 4428.097 | 4289.8 | 1175.512
| Jul | 3716.492 | 3672.762 | 960.394 |  | Jul | 450.112 | 430.01 | 120.093 |  | Jul | 132.738 | 124.38 | 35.244 |  | Jul | 100.371 | 94.056 | 27.124 |  | Jul | 4399.713 | 4321.208 | 1142.855
| Aug | 3809.054 | 3758.138 | 937.144 |  | Aug | 461.154 | 440.67 | 124.045 |  | Aug | 134.861 | 129.216 | 36.133 |  | Aug | 98.378 | 94.14 | 25.64 |  | Aug | 4503.447 | 4422.164 | 1122.962
| Sept | 3715.461 | 3666.122 | 952.187 |  | Sept | 443.703 | 423.59 | 123.222 |  | Sept | 128.175 | 122.868 | 34.818 |  | Sept | 98.754 | 98.313 | 24.873 |  | Sept | 4386.093 | 4310.893 | 1135.1
| Oct | 3876.886 | 3727.302 | 984.011 |  | Oct | 449.341 | 429.01 | 123.984 |  | Oct | 138.164 | 132.24 | 37.606 |  | Oct | 94.901 | 90.036 | 27.203 |  | Oct | 4559.292 | 4378.588 | 1172.804
| Nov | 3698.458 | 3610.262 | 911.086 |  | Nov | 419.72 | 400.42 | 113.994 |  | Nov | 127.824 | 122.592 | 35.636 |  | Nov | 86.705 | 84.756 | 25.71 |  | Nov | 4332.707 | 4218.03 | 1086.426
| Dec | 3777.814 | 3727.302 | 939.134 |  | Dec | 454.684 | 423.41 | 121.543 |  | Dec | 138.993 | 133.092 | 37.793 |  | Dec | 101.858 | 94.992 | 28.43 |  | Dec | 4473.349 | 4378.796 | 1126.9
2007 | Jan | 4037.888 | 3942.361 | 996.784 | 2007 | Jan | 473.976 | 451.42 | 121.543 | 2007 | Jan | 132.08 | 126.18 | 36.798 | 2007 | Jan | 95.405 | 91.404 | 27.394 | 2007 | Jan | 4739.349 | 4611.365 | 1182.519
| Feb | 3895.636 | 3811.987 | 967.277 |  | Feb | 437.036 | 417.07 | 121.544 |  | Feb | 126.621 | 121.404 | 35.027 |  | Feb | 98.806 | 85.344 | 25.131 |  | Feb | 4558.099 | 4435.805 | 1148.979
| Mar | 4009.831 | 3942.655 | 1013.55 |  | Mar | 474.232 | 452.38 | 130.576 |  | Mar | 143.972 | 137.652 | 38.88 |  | Mar | 109.319 | 97.176 | 29.561 |  | Mar | 4737.354 | 4629.863 | 1212.567
| Apr | 3838.703 | 3761.259 | 950.485 |  | Apr | 436.29 | 415.34 | 120.822 |  | Apr | 135.434 | 129.624 | 36.699 |  | Apr | 106.108 | 92.748 | 28.214 |  | Apr | 4516.535 | 4398.971 | 1136.22
| May | 4139.75 | 4044.282 | 1009.345 |  | May | 478.206 | 455.86 | 139.525 |  | May | 135.539 | 131.232 | 37.788 |  | May | 119.387 | 107.544 | 32.57 |  | May | 4872.882 | 4738.918 | 1219.228
| Jun | 3927.478 | 3754.515 | 955.83 |  | Jun | 454.699 | 432.91 | 133.952 |  | Jun | 132.2 | 126.852 | 36.129 |  | Jun | 109.355 | 95.448 | 29.746 |  | Jun | 4623.732 | 4409.725 | 1155.657
| Jul | 3636.76 | 3550.004 | 928.122 |  | Jul | 446.891 | 425.31 | 130.311 |  | Jul | 134.264 | 128.088 | 36.289 |  | Jul | 110.897 | 98.244 | 30.201 |  | Jul | 4328.812 | 4201.646 | 1124.923
| Aug | 3895.094 | 3801.91 | 914.772 |  | Aug | 469.017 | 447.03 | 135.558 |  | Aug | 131.813 | 126.264 | 36.051 |  | Aug | 104.8 | 95.652 | 30.077 |  | Aug | 4600.724 | 4470.856 | 1116.458
| Sept | 4038.522 | 3953.59 | 973.048 |  | Sept | 455.757 | 425.23 | 127.413 |  | Sept | 130.727 | 126.072 | 36.228 |  | Sept | 103.878 | 91.284 | 29.639 |  | Sept | 4728.884 | 4596.176 | 1166.328
| Oct | 4262.203 | 4158.09 | 1034.857 |  | Oct | 469.653 | 447.04 | 132.767 |  | Oct | 136.615 | 130.452 | 38.028 |  | Oct | 105.997 | 92.988 | 31.216 |  | Oct | 4974.468 | 4828.57 | 1236.868
| Nov | 4046.032 | 3931.733 | 987.25 |  | Nov | 453.369 | 432.97 | 129.076 |  | Nov | 128.201 | 122.916 | 36.236 |  | Nov | 102.765 | 90.48 | 29.616 |  | Nov | 4730.367 | 4578.099 | 1182.178
| Dec | 4308.081 | 4182.188 | 1040.362 |  | Dec | 467.074 | 457 | 122.966 |  | Dec | 135.61 | 129.828 | 37.517 |  | Dec | 112.375 | 99.708 | 32.618 |  | Dec | 5023.14 | 4868.724 | 1233.463
2008 | Jan | 4334.248 | 4210.962 | 1058.569 | 2008 | Jan | 467.744 | 436.61 | 130.162 | 2008 | Jan | 136.068 | 131.388 | 38.555 | 2008 | Jan | 109.853 | 97.092 | 31.832 | 2008 | Jan | 5047.913 | 4876.052 | 1259.118 | 56781.701 | 14186.248
| Feb | 4263.694 | 4138.878 | 1043.076 |  | Feb | 436.374 | 415.78 | 124.954 |  | Feb | 127.725 | 122.328 | 35.43 |  | Feb | 99.064 | 87.312 | 28.252 |  | Feb | 4926.857 | 4764.298 | 1231.712
| Mar | 4403.129 | 4276.818 | 1073.646 |  | Mar | 442.06 | 421.5 | 126.733 |  | Mar | 135.074 | 130.38 | 35.651 |  | Mar | 105.929 | 95.004 | 30.294 |  | Mar | 5086.192 | 4923.702 | 1266.324
| Apr | 4385.466 | 4233.962 | 1079.063 |  | Apr | 431.89 | 411.57 | 122.35 |  | Apr | 124.896 | 123.899 | 37.383 |  | Apr | 94.504 | 85.932 | 26.209 |  | Apr | 5036.756 | 4855.363 | 1265.005
| May | 4036.783 | 3872.021 | 984.148 |  | May | 459.389 | 437.1 | 128.247 |  | May | 118.599 | 116.988 | 36.014 |  | May | 99.675 | 89.22 | 28.135 |  | May | 4714.446 | 4515.329 | 1176.544
| Jun | 3892.946 | 3769.73 | 949.734 |  | Jun | 420.937 | 399.98 | 116.655 |  | Jun | 116.283 | 114.672 | 34.009 |  | Jun | 93.133 | 82.152 | 24.659 |  | Jun | 4523.299 | 4366.534 | 1125.057
| Jul | 3879.204 | 3780.701 | 924.765 |  | Jul | 412.677 | 391.83 | 116.172 |  | Jul | 114.468 | 114.048 | 35.067 |  | Jul | 95.278 | 82.476 | 28.887 |  | Jul | 4501.627 | 4369.055 | 1104.891
| Aug | 4074.075 | 3933.261 | 998.195 |  | Aug | 460.325 | 438.95 | 127.634 |  | Aug | 126.24 | 120.893 | 35.901 |  | Aug | 99.156 | 85.788 | 30.711 |  | Aug | 4759.796 | 4578.892 | 1192.441
| Sept | 3704.813 | 3582.349 | 918.029 |  | Sept | 405.401 | 387.12 | 111.827 |  | Sept | 108.624 | 102.688 | 34.62 |  | Sept | 89.011 | 84.972 | 23.031 |  | Sept | 4307.849 | 4157.129 | 1087.507
| Oct | 3920.271 | 3796.975 | 960.276 |  | Oct | 436.228 | 416.15 | 120.912 |  | Oct | 112.567 | 110.352 | 34.77 |  | Oct | 89.385 | 87.348 | 24.375 |  | Oct | 4558.451 | 4410.825 | 1140.333
| Nov | 4046.076 | 3920.54 | 998.757 |  | Nov | 405.303 | 386.49 | 112.053 |  | Nov | 110.184 | 109.452 | 33.254 |  | Nov | 89.126 | 86.016 | 22.749 |  | Nov | 4650.689 | 4502.498 | 1166.813
| Dec | 4014.071 | 3896.785 | 990.144 |  | Dec | 435.641 | 394.42 | 117.393 |  | Dec | 119.514 | 118.814 | 35.857 |  | Dec | 98.6 | 95.64 | 27.109 |  | Dec | 4667.826 | 4505.659 | 1170.503
2009 | Jan | 4268.966 | 4130.852 | 1062.867 | 2009 | Jan | 386.802 | 368.82 | 113.67 | 2009 | Jan | 114.859 | 112.848 | 35.252 | 2009 | Jan | 97.842 | 95.844 | 27.706 | 2009 | Jan | 4868.469 | 4708.364 | 1239.495 | 52631.366 | 13188.8313
| Feb | 3983.317 | 3870.821 | 981.386 |  | Feb | 409.998 | 388.21 | 105.427 |  | Feb | 109.124 | 107.1 | 32.8 |  | Feb | 88.419 | 85.512 | 24.984 |  | Feb | 4590.858 | 4451.643 | 1144.597
| Mar | 4360.845 | 4247.953 | 1065.31 |  | Mar | 423.573 | 403.27 | 115.363 |  | Mar | 124.817 | 121.944 | 36.437 |  | Mar | 97.628 | 95.688 | 26.6033 |  | Mar | 5006.863 | 4868.855 | 1243.7133
| Apr | 3631.531 | 3581.134 | 893.196 |  | Apr | 393.965 | 374.95 | 107.921 |  | Apr | 113.663 | 110.016 | 32.905 |  | Apr | 91.08 | 87.804 | 24.408 |  | Apr | 4230.239 | 4153.904 | 1058.43
| May | 3885.111 | 3835.145 | 951.385 |  | May | 417.71 | 397.98 | 125.005 |  | May | 130.41 | 127.656 | 36.439 |  | May | 98.142 | 94.932 | 26.553 |  | May | 4531.373 | 4455.713 | 1139.382
| Jun | 3396.807 | 3357.219 | 835.557 |  | Jun | 387.516 | 369.22 | 110.279 |  | Jun | 113.212 | 110.052 | 30.975 |  | Jun | 87.006 | 85.536 | 23.915 |  | Jun | 3984.541 | 3922.027 | 1000.726
| Jul | 3667.979 | 3626.176 | 900.528 |  | Jul | 417.977 | 398.89 | 114.606 |  | Jul | 119.116 | 115.344 | 32.982 |  | Jul | 90.3 | 88.32 | 25.838 |  | Jul | 4295.372 | 4228.73 | 1073.954
| Aug | 3573.095 | 3531.576 | 889.46 |  | Aug | 423.183 | 403.01 | 116.131 |  | Aug | 117.656 | 112.44 | 30.999 |  | Aug | 91.9 | 89.604 | 25.34 |  | Aug | 4205.834 | 4136.63 | 1061.93
| Sept | 3493.604 | 3454.668 | 855.577 |  | Sept | 410.744 | 391.74 | 111.185 |  | Sept | 114.944 | 109.392 | 28.979 |  | Sept | 86.3 | 83.964 | 23.401 |  | Sept | 4105.592 | 4039.764 | 1019.142
| Oct | 3565.825 | 3518.026 | 909.499 |  | Oct | 413.738 | 394.43 | 113.366 |  | Oct | 120.031 | 115.38 | 31.038 |  | Oct | 87.408 | 83.364 | 25.3 |  | Oct | 4187.002 | 4111.2 | 1079.203
| Nov | 3528.811 | 3409.379 | 855.455 |  | Nov | 403.621 | 384.53 | 110.307 |  | Nov | 114.188 | 109.98 | 30.476 |  | Nov | 84.238 | 80.616 | 23.836 |  | Nov | 4130.858 | 3984.505 | 1020.074
| Dec | 3857.683 | 3728.11 | 931.87 |  | Dec | 427.228 | 406.81 | 118.628 |  | Dec | 118.064 | 113.7 | 31.026 |  | Dec | 91.39 | 88.164 | 26.661 |  | Dec | 4494.365 | 4336.784 | 1108.185
2010 | Jan | 4131.364 | 3999.095 | 1007.503 | 2010 | Jan | 441.031 | 419.66 | 122.047 | 2010 | Jan | 125.708 | 120.624 | 34.641 | 2010 | Jan | 95.784 | 92.016 | 26.993 | 2010 | Jan | 4793.887 | 4631.395 | 1191.184 | 52612.052 | 13086.288
| Feb | 3408.861 | 3310.953 | 841.062 |  | Feb | 308.713 | 291.83 | 84.723 |  | Feb | 94.233 | 90.78 | 26.198 |  | Feb | 70.483 | 67.704 | 18.96 |  | Feb | 3882.29 | 3761.267 | 970.943
| Mar | 3886.532 | 3830.995 | 1003.699 |  | Mar | 414.079 | 393.06 | 114.499 |  | Mar | 126.521 | 121.5 | 34.349 |  | Mar | 90.385 | 86.28 | 24.329 |  | Mar | 4517.517 | 4431.835 | 1176.876
| Apr | 3852.922 | 3730.76 | 925.994 |  | Apr | 392.722 | 372.57 | 109.964 |  | Apr | 120.483 | 115.608 | 33.208 |  | Apr | 89.647 | 85.956 | 24.098 |  | Apr | 4455.774 | 4304.894 | 1093.264
| May | 3861.173 | 3730.147 | 937.261 |  | May | 396.344 | 382.512 | 125.223 |  | May | 127.827 | 122.04 | 33.343 |  | May | 90.455 | 98.196 | 27.4 |  | May | 4475.799 | 4332.895 | 1123.227
| Jun | 3719.277 | 3594.692 | 896.474 |  | Jun | 403.046 | 383.085 | 104.523 |  | Jun | 121.858 | 116.28 | 32.202 |  | Jun | 83.8 | 81.204 | 21.94 |  | Jun | 4327.981 | 4175.261 | 1055.139
| Jul | 3670.139 | 3544.762 | 877.334 |  | Jul | 432.465 | 411.602 | 110.998 |  | Jul | 125.071 | 119.652 | 34.029 |  | Jul | 89.272 | 88.5 | 24.05 |  | Jul | 4316.947 | 4164.516 | 1046.411
| Aug | 3695.793 | 3581.03 | 904.139 |  | Aug | 430.127 | 409.954 | 110.253 |  | Aug | 123.903 | 118.62 | 32.348 |  | Aug | 90.924 | 87.48 | 24.38 |  | Aug | 4340.747 | 4197.084 | 1071.12
| Sept | 3648.033 | 3539.886 | 889.991 |  | Sept | 423.154 | 403.652 | 108.188 |  | Sept | 121.757 | 117.144 | 33.167 |  | Sept | 85.463 | 82.164 | 23.509 |  | Sept | 4278.407 | 4142.846 | 1054.855
| Oct | 3777.618 | 3656.852 | 920.756 |  | Oct | 426.885 | 422.165 | 111.32 |  | Oct | 129.837 | 124.692 | 34.775 |  | Oct | 91.745 | 88.668 | 25.654 |  | Oct | 4426.085 | 4292.377 | 1092.505
| Nov | 3640.895 | 3533.041 | 883.291 |  | Nov | 387.153 | 382.896 | 101.401 |  | Nov | 121.594 | 116.688 | 32.889 |  | Nov | 88.944 | 85.102 | 24.584 |  | Nov | 4238.586 | 4117.727 | 1042.165
| Dec | 3921.814 | 3796.304 | 996.497 |  | Dec | 414.029 | 409.509 | 110.358 |  | Dec | 125.152 | 120.336 | 34.101 |  | Dec | 97.037 | 93.876 | 27.643 |  | Dec | 4558.032 | 4420.025 | 1168.599
2011 | Jan | 4377.459 | 4250.425 | 1082.89 | 2011 | Jan | 410.8816 | 404.6416 | 107.674 | 2011 | Jan | 112.453 | 110.64 | 29.623 | 2011 | Jan | 96.23 | 93.42 | 24.918 | 2011 | Jan | 4997.0236 | 4859.1266 | 1245.105
| Feb | 3304.168 | 3208.147 | 817.389 |  | Feb | 364.8082 | 359.2162 | 95.9874 |  | Feb | 106.539 | 104.76 | 28.0296 |  | Feb | 86.109 | 83.976 | 22.699 |  | Feb | 3861.6242 | 3756.0992 | 964.1049
| Mar | 4151.518 | 4041.298 | 1028.2463 |  | Mar | 422.5597 | 413.9197 | 110.254 |  | Mar | 125.323 | 123.252 | 34.349 |  | Mar | 95.414 | 92.892 | 24.886 |  | Mar | 4794.8147 | 4671.3617 | 1197.7353
| Apr | 3915.016 | 3801.891 | 969.8645 |  | Apr | 407.494 | 400.294 | 105.668 |  | Apr | 119.6 | 117.744 | 33.208 |  | Apr | 94.515 | 92.244 | 27.673 |  | Apr | 4536.625 | 4412.173 | 1136.4135
| May | 3833.492 | 3770.893 | 962.2408 |  | May | 443.1398 | 435.8598 | 115.61 |  | May | 122.258 | 120.492 | 34.1896 |  | May | 98.428 | 95.76 | 25.8 |  | May | 4497.3178 | 4423.0048 | 1137.8404
| Jun | 3706.703 | 3598.063 | 906.0054 |  | Jun | 394.2084 | 389.3284 | 102.916 |  | Jun | 115.028 | 113.292 | 32.1137 |  | Jun | 100.21 | 97.836 | 29.1 |  | Jun | 4316.1494 | 4198.5194 | 1070.1351
| Jul | 3637.951 | 3525.528 | 887.1607 |  | Jul | 401.427 | 397.507 | 104.8107 |  | Jul | 119.431 | 117.576 | 32.4764 |  | Jul | 103.449 | 99.96 | 28.474 |  | Jul | 4262.258 | 4140.571 | 1052.9219
| Aug | 3587.169 | 3490.954 | 878.4207 |  | Aug | 409.2356 | 402.9956 | 106.6815 |  | Aug | 120.021 | 117.984 | 32.541 |  | Aug | 96.058 | 93.804 | 27.0603 |  | Aug | 4212.4836 | 4105.7376 | 1044.7035
| Sept | 3407.892 | 3301.107 | 829.983 |  | Sept | 400.668 | 394.108 | 106.7691 |  | Sept | 112.547 | 110.892 | 30.756 |  | Sept | 92.614 | 90.228 | 25.543 |  | Sept | 4013.721 | 3896.335 | 993.0511
| Oct | 3742.854 | 3630.815 | 916.85 |  | Oct | 422.147 | 415.827 | 111.9266 |  | Oct | 117.064 | 115.26 | 31.519 |  | Oct | 92.627 | 90.744 | 25.506 |  | Oct | 4374.692 | 4252.646 | 1085.8016
| Nov | 3744.898 | 3635.142 | 915.9615 |  | Nov | 395.1884 | 388.1484 | 103.3378 |  | Nov | 110.625 | 108.864 | 29.7814 |  | Nov | 89.698 | 86.808 | 24.4347 |  | Nov | 4340.4094 | 4218.9624 | 1073.5153
| Dec | 3988.923 | 3875.726 | 976.8841 |  | Dec | 427.9346 | 420.8146 | 117.2871 |  | Dec | 117.34 | 115.584 | 32.2839 |  | Dec | 104.976 | 102.792 | 28.14 |  | Dec | 4639.1736 | 4514.9166 | 1154.5951
2012 | Jan | 4100.835 | 4005.875 | 1005.8788 | 2012 | Jan | 434.6072 | 427.7272 | 118.9013 | 2012 | Jan | 119.987 | 117.984 | 31.9513 | 2012 | Jan | 93.851 | 90.876 | 25.4433 | 2012 | Jan | 4749.2802 | 4642.4622 | 1182.1746
| Feb | 3507.091 | 3430.667 | 865.4269 |  | Feb | 368.546 | 363.346 | 100.1613 |  | Feb | 105.853 | 104.28 | 29.3801 |  | Feb | 86.17 | 83.832 | 23.9 |  | Feb | 4067.66 | 3982.125 | 1018.8683
| Mar | 4125.412 | 4024.688 | 1016.2879 |  | Mar | 428.6883 | 422.2083 | 116.2668 |  | Mar | 120.868 | 118.848 | 33.9115 |  | Mar | 100.155 | 97.548 | 27.501 |  | Mar | 4775.1233 | 4663.2923 | 1193.9671
| Apr | 3835.524 | 3736.68 | 943.3005 |  | Apr | 403.8089 | 397.5689 | 102.6436 |  | Apr | 116.749 | 115.176 | 32.2011 |  | Apr | 89.856 | 87.672 | 24.3 |  | Apr | 4445.9379 | 4337.0969 | 1102.4452
| May | 3732.94 | 3639.781 | 911.08 |  | May | 419.214 | 412.894 | 120.063 |  | May | 133.43 | 131.136 | 36.075 |  | May | 95.321 | 93.012 | 26.206 |  | May | 4380.905 | 4276.823 | 1093.424
| Jun | 3533.301 | 3441.561 | 857.6 |  | Jun | 419.214 | 412.894 | 100.047 |  | Jun | 107.369 | 105.54 | 28.259 |  | Jun | 91.753 | 88.992 | 25.299 |  | Jun | 4151.637 | 4048.987 | 1011.205
| Jul | 3555.351 | 3471.037 | 866.88 |  | Jul | 419.214 | 412.894 | 102.558 |  | Jul | 112.172 | 110.268 | 29.353 |  | Jul | 91.606 | 89.424 | 25.304 |  | Jul | 4178.343 | 4083.623 | 1024.095
| Aug | 3596.221 | 3502.334 | 848.331 |  | Aug | 419.214 | 412.894 | 103.069 |  | Aug | 117.919 | 115.957 | 32.376 |  | Aug | 94.504 | 92.268 | 25.901 |  | Aug | 4227.858 | 4123.453 | 1009.677
| Sept | 3546.11 | 3457.643 | 824.629 |  | Sept | 419.214 | 412.894 | 101.644 |  | Sept | 103.674 | 101.941 | 28.703 |  | Sept | 90.635 | 88.812 | 24.713 |  | Sept | 4159.633 | 4061.29 | 979.689
| Oct | 3729.916 | 3639.937 | 874.12 |  | Oct | 419.214 | 412.894 | 108.429 |  | Oct | 120.968 | 119.038 | 31.241 |  | Oct | 94.648 | 92.741 | 27.139 |  | Oct | 4364.746 | 4264.61 | 1040.929
| Nov | 3713.643 | 3625.627 | 868.938 |  | Nov | 419.214 | 412.894 | 104.051 |  | Nov | 113.85 | 111.95 | 31.731 |  | Nov | 89.128 | 87.41 | 23.739 |  | Nov | 4335.835 | 4237.881 | 1028.459
| Dec | 3962.549 | 3853.939 | 921.9308 |  | Dec | 427.5633 | 420.4433 | 108.4722 |  | Dec | 124.244 | 122.209 | 34.2406 |  | Dec | 95.715 | 93.887 | 26.9117 |  | Dec | 4610.0713 | 4490.4783 | 1091.5553