## Source
Selected tables extracted from the Pacific Power utilities benchmarking report. Published in 2011 with 2010 data coverage
REPORT WAS PREPARED BY THE PACIFIC POWER ASSOCIATION (PPA) WITH THE SUPPORT OF THE PACIFIC INFRASTRUCTURE ADVISORY CENTRE (PIAC) AND THE SECRETARIAT OF THE PACIFIC COMMUNITY (SPC)
http://prdrse4all.spc.int/system/files/final_report_2011-_benchmarking_for_pacific_power_utilities.pdf

## Content
Content
Table 2.1 | Economies and populations of independent Pacific Island countries
Table 2.2 | Economies and populations of Pacific Island territories or dependencies
Table 2.3 | Utility Participation in 2011 benchmarking
Table 2.4 | Basic information on participating utilities in 2010
Table 2.5 | Utility electricity sales in 2010 (GWh)
Table 2.6 | Gross generation by source - for main grid only - in 2010 (MWh)
Table 2.7a | Utility structures, ownership, policies, regulation and coverage
Table 2.7b | Utility structures, ownership, policies, regulation and coverage
Table 2.7c | Utility structures, ownership, policies, regulation and coverage
Tab 2.7a-c | Summerised Information from Table 2.7a-c
Table 2.8 | Utility transmission and distribution voltages (kV)
Table 3.1 | Key benchmark indicators (2000 & 2010)
Table 3.2 | Additional indicators or information requested for 2011 benchmarking | table not captured
Table 4.1 | Utility participation 2010 and 2000 | table not captured
Table 4.2 | Utility demand side management efforts in 2010
Table 4.3 | Composite indicator suggestive of utility technical performance
Table 5.1 | Key indicators compared for 2002 and 2011 Pacific benchmarking reports
Table 5.2 | Key indicators compared for Pacific and other small utilities
Table 7.1 | Revised Pacific regional benchmarking indicators and goals for CEOs consideration
Appendix | Data Tables

## Tab 2.1
content
Table 2.1 Economies and populations of independent Pacific Island countries
| Country | Population | Land Area | GNP per capita | GDP per capita |  | GDP growth per capita |  | Current account balance | High exposure to fuel price rises
|  | mid 2011 | km2 | US$;2009 | US$ | Year | % 2010 | % 2011 | % GDP; 2010
| CookIsl. | 15576 | 237 | n.a. | 10875 | 2008 | -2.2 | -0.8 | 4.9 | √
| Fiji | 851745 | 18273 | 3840 | 3499 | 2008 | -0.3 | 0 | -2.3 | √
| Kiribati | 102697 | 811 | 1830 | 1490 | 2008 | -1.2 | 0.1 | -13.7 | √
| MarshallIslands | 54999 | 181 | 3060 | 2851 | 2007 | -1 | 0 | -10.5 | √
| Micronesia,Fed. States | 102360 | 701 | 2500 | 2183 | 2007 | -7.6 | n.a. | -17 | √
| Nauru | 10185 | 21 | n.a. | 2071 | 2006/7 | 0 | 1.9 | n.a. | √
| Palau | 20643 | 444 | 6220 | 8423 | 2007 | 1.4 | n.a. | -9.5 | √
| PNG | 6888297 | 462840 | 1180 | 897 | 2006 | 4.8 | 6.2 | -26.6 | √
| Samoa | 183617 | 2785 | 2840 | 2672 | 2008 | -0.3 | 2.7 | -8.1 | √
| SolomonIslands | 553254 | 30407 | n.a. | 1014 | 2008 | 1.6 | 5.2 | -20 | √
| Tonga | 103682 | 650 | 3260 | 2629 | 2007/8 | -1.5 | 0.2 | -5.6 | √
| Tuvalu | 11206 | 26 | n.a. | 1831 | 2002 | -0.5 | -0.5 | n.a. | √
| Vanuatu | 251784 | 12281 | 2620 | 2218 | 2007 | 0.7 | 1.2 | -2.4% | √
| PIC Avergae |  |  | 3038.8889 | 3281 |  | -0.5% | 1.5%
| CARICOM average |  |  |  | 11632 | various
Notes: 1. e = estimated 2. n.a. = not available 3. Utilities from all above PICs above participated in 2011 benchmarking.
Sources: 1. Asian Development Bank (ADB). 2011. Asian Development Outlook 2. ADB. 2011. Pacific Economic Monitor 3. GNPs from ADB; GDPs from Secretariat of the Pacific Community (SPC). 2010. Pocket Summary 4. SPC. 2011. Populations from Pacific Island Populations: Estimates and Projections 5. CARICOM GDPs sourced from CIA. 2011. The World Factbook. https://www.cia.gov/library/publications/the-worldfactbook/geos/xx.html

## Tab 2.2
content
Table 2.2: Economies and populations of Pacific Island territories or dependencies5
| Dependency or Territory | Population Mid-2011 | Land area km2 | GDP per capita
|  |  |  | US$ | Year
| AmericanSamoa | 66692 | 199 | 9041 | 2005
| Guam | 192090 | 541 | 22661 | 2005
| Niue | 1446 | 259 | 9618 | 2006
| NorthernMarianaIsl | 63517 | 457 | 12638 | 2005
| NewCaledonia | 252331 | 18576 | 37993 | 2008
| FrenchPolynesia | 271831 | 3521 | 21071 | 2006
| Wallis&Futuna | 13193 | 142 | n.a. | n.a.
| Average |  |  | 18837
Sources: 1. Asian Development Bank (ADB). 2011. Asian Development Outlook 2. ADB. 2011. Pacific Economic Monitor 3. GNPs from ADB; GDPs from Secretariat of the Pacific Community (SPC). 2010. Pocket Summary 4. SPC. 2011. Populations from Pacific Island Populations: Estimates and Projections 5. CARICOM GDPs sourced from CIA. 2011. The World Factbook. https://www.cia.gov/library/publications/the-world-factbook/geos/xx.html.
5. French Polynesia was designated as an overseas territory, in 2003 became an overseas collectively (collectivités d'outremer or COM) and in 2004 an overseas country inside the French Republic (pays d'outre-mer au sein de la République, or POM), with considerable autonomy but without a legal modification of its status. New Caledonia was also an overseas territory but gained a special status (statut particulier or statut original) in 1999, with New Caledonian citizenship and a gradual transfer of power from France to New Caledonia itself.

## Tab 2.3
content
Table 2.3 Utility participation in 2011 benchmarking
| Abreviation | Utility | Country Territory
Particitpating Countries
1 | ASPA | American Samoa Power Authority | American Samoa (US territory)
2 | CPUC | Chuuk Public Utility Corporation | Federated States of Micronesia (FSM)
3 | CUC | Commonwealth Utilities Corporation | Commonwealth of Northern Marianas
4 | EDT | Electricité de Tahiti | French Polynesia (Polynésie Française) (COM)**
5 | EPC | Electric Power Corporation | Samoa (SAM)
6 | FEA | Fiji Electricity Authority | Republic of Fiji (FIJ)
7 | GPA | Guam Power Authority | Guam (US territory)
8 | KAJUR* | Kwajalein Atoll Joint Utility Resources | Republic of Marshall Islands (RMI)
9 | KUA | Kosrae Utilities Authority | Federated States of Micronesia (FSM)
10 | MEC* | Marshall Energy Company | Republic of Marshall Islands (RMI)
11 | NPC | Niue Power Corporation | Niue
12 | NUA | Nauru Utilities Corporation | Republic of Nauru (NAU)
13 | PPL | PNG Power Ltd. | Papua New Guinea (PNG)
14 | PPUC | Palau Public Utilities Corporation | Republic of Palau (PAL)
15 | PUB | Public Utilities Board | Republic of Kiribati (KIR)
16 | SIEA | Solomon Islands Electricity Authority | Solomon Islands (SOL)
17 | TAU | Te Aponga Uira O Tumu -Te-Varovaro | Cook Islands (COO)
18 | TEC | Tuvalu Electricity Corporation | Tuvalu (TUV)
19 | TPL | Tonga Power Limited | Tonga (TON)
20 | UNELCO | UNELCO Vanuatu Limited | Vanuatu
21 | YSPSC | Yap State Public Service Corporation | Federated States of Micronesia (FSM)
Non-Participating Utilities
1 | EEC | Electricité et Eau de Caledonie | New Caledonia (Nouvelle Calédonie)
2 | EEWF | Electricité et Eau de Wallis et Futuna | Wallis and Futuna (Wallis et Futuna)
3 | ENERCAL | Societe Neo-Caledonenne D’Energie | New Caledonia (Nouvelle Calédonie)
4 | HECO | Hawaii Electric Company | Hawaii (USA) (US territory)
5 | PUC | Pohnpei Utilities Corporation | Federated States of Micronesia (FSM)
Notes: 1. The bracketed abbreviations are ADB designations for its Pacific developing member countries 2. * Indicates that limited data were provided so some key indicators could not be calculated 3. ** For explanation of the designation ‘COM’, see footnote 5.

## Tab 2.4
content
Table 2.4: Basic information on participating utilities in 2010
| Utility | Installed Capacity | Gross generation excludes IPPS | Maximum Demand | Minimum Demand | Customers (Number) | Employees (full-time equivalent)
|  | (MW) | (MWh) | (MW) | (MW)
| ASPA (A. Samoa) | 47.7 | 159113 | 24.8 | 13 | 11884 | 209
| CPUC (Chuuk, FSM) | 2 | 9768 | 4 | - | 1634 | 56
| CUC (Saipan) | 106.7 | 216541 | 44.9 | 37 | 15500 | 242
| EDT (Tahiti) | 235.3 | 688853 | 101.4 | 44.8 | 81044 | 487
| EPC (Samoa) | 37.5 | 111353 | 18 | 6.4 | 38158 | 602
| FEA (Fiji) | 211.2 | 835169 | 139.6 | 60 | 151410 | 673
| GPA (Guam) | 552.8 | 1252672 | 272 | 139 | 47333 | 522
| KAJUR (Ebeye, RMI) | 3.6 | 14183 | 2 | - | - | -
| KUA (Kosrae, FSM) | 5 | 6504 | 1.1 | 0.6 | 1845 | 23
| MEC (Majuro, RMI) | 28 | 75747 | 8.9 | 6.5 | 4832 | 180
| NPC (Niue) | 2.1 | 3000 | 0.6 | 0.3 | 870 | 21
| NUA (Nauru) | 8 | 17103 | 3.3 | 1.7 | 1918 | 70
| PPL (PNG) | 292 | 796610 | 92.9 | 33 | 91173 | 1412
| PPUC (Palau) | 18.9 | 84860 | 15.4 | - | 6417 | 70
| PUB (Kiribati) | 5.5 | 21641 | 5.3 | 2 | 8337 | 57
| SIEA (SolomonIsl) | 25.6 | 83600 | 13.8 | 4.9 | 13753 | –
| TAU (CookIslands) | 10.36 | 27763 | 4.9 | 3.4 | 5249 | 54
| TEC (Tuvalu) | 5.1 | 11800 | 1 | 0.5 | 2210 | 59
| TPL (Tonga) | 15.3 | 52609 | 7.7 | 3.1 | 14000 | 104
| UNELCO (Vanuatu) | 23.6 | 60360 | 11.3 | 2.4 | 10571 | 106
| YSPSC(Yap,FSM) | 6.6 | 13000 | 2.3 | 1.3 | 1900 | 23
| Average | 80 | 219200 | 37.5 | 20.4 | 26200 | 265
| Median | 17 | 56500 | 8.3 | 3.4 | 8300 | 87
Notes: 1. For Tables 2.4 - 2.7 data were provided by the utilities. However some data provided were inconsistent (or reported differently in different parts of the questionnaire) so some data in other tables may differ 2. Blank cells = data were unavailable in time for this draft report 3. Averages & medians only calculated for those with data in the cells, and are rounded off.

## Tab 2.5
content
Table 2.5: Utility electricity sales in 2010 (GWh)
| Utility | Household | Commercial | Industry | Other (include govt) | Total
| ASPA (A. Samoa) | 45.3 | 40.6 | 20.6 | 35.4 | 141.9
| CPUC (Chuuk, FSM) | 3.2 | 2.3 | 0 | 0.9 | 6.4
| CUC (Saipan) | 77.74 | 131.1 | 0 | 63 | 271.84
| EDT (Tahiti) | 229.7 | 105.3 | 292.1 | 9 | 636.2
| EPC (Samoa) | 25.7 | 52.9 | 4.8 | 8.3 | 91.7
| FEA (Fiji) | 215.8 | 336.7 | 190.2 | 12.1 | 754.8
| GPA (Guam) | 487 | 578.3 | 0 | 572.3 | 1637.6
| KAJUR (Ebeye, RMI) | n.a | n.a | n.a | n.a | n.a
| KUA (Kosrae, FSM) | 2.2 | 1.48 | 0.33 | 1.53 | 5.53
| MEC (Majuro, RMI) | n.a | n.a | n.a | n.a | 55.38**
| NPC (Niue) | n.a. | n.a | n.a | n.a | 2.79**
| NUA (Nauru) | n.a | n.a | n.a | n.a | 13.27**
| PPL (PNG) | 147 | 444 | 166 | 0 | 757
| PPUC (Palau) | 22.8 | 24.6 | 0 | 19.7 | 67.1
| PUB (Kiribati) | 7.14 | 3 | 7 | 3.4 | 20.54
| SIEA (SolomonIsl) | 9.6 | 29.7 | 7.8 | 10.1 | 57.2
| TAU (CookIslands) | 8.11 | 16.46 | 0 | 0.28 | 24.85
| TEC (Tuvalu) | 2.43 | 1.52 | 0 | 1.46 | 5.41
| TPL (Tonga) | 17.9 | 17.05 | 2.98 | 4.69 | 42.62
| UNELCO (Vanuatu) | 17 | 14 | 21 | 5 | 57
| YSPSC(Yap,FSM) | 2.18 | 1.48 | 0.33 | 1.53 | 5.51
| % of Total * | 29% | 39% | 16% | 16% | 100%
Notes: 1. * Calculated only for utilities that provided sales by customer category 2. ** Data from annual reports, donor studies, governments, etc., not from utility benchmark questionnaire 3. The definition of ‘commercial’ differs by utility: some include government sales within commercial 4. n.a. = not available from utility data provided.

## Tab 2.6
content
Table 2.6: Gross generation by source - for main grid only - in 2010 (MWh)
| Utility | Distillate ADO / IDO** | Heavy fuel HFO / IFO*** | Hydro | Wind | Solar PV | Biomass & Biofuel | Total | %RE*
| ASPA (A. Samoa) | 159113 | - | - | - | - | - | 159113 | 0
| CPUC (Chuuk, FSM) | - | 9798 | - | - | - | - | 9798 | 0
| CUC (Saipan) | 208446 | - | - | - | - | - | 208446 | 0
| EDT (Tahiti) | 4245 | 336002 | 209145 | - |  |  | 549392 | 38.1
| EPC (Samoa) | 51663 |  | 47738 |  | 4 | 156 | 99561 | 48.1
| FEA (Fiji) | 236356 | 126237 | 413619 | 6420 |  | 16207 | 798839 | 54.6
| GPA (Guam) | 26122 | 1835881 | - | - | - | - | 1862003 | 0
| KAJUR (Ebeye, RMI) | - | - | - | - | - | - | 0
| KUA (Kosrae, FSM) | 6504 | - | - | - | 56 | - | 6560 | 0.9
| MEC (Majuro, RMI) | 62912 | - | - | - | - | - | 62912 | 0
| NPC (Niue) | 3000 | - | - | - | 3 | - | 3003 | 0.1
| NUA (Nauru) | 23187 | - | - | - | 53 | - | 23240 | 0.2
| PPL (PNG) | 31734 | 16333 | 283454 | - | - | - | 331521 | 85.5
| PPUC (Palau) | 83075 | - | - | - | - | - | 83075 | 0
| PUB (Kiribati) | 21641 | - | - | - | - | - | 21641 | 0
| SIEA (SolomonIsl) | 83623 | - | - | - | - | 180 | 83803 | 0.2
| TAU (CookIslands) | 27763 | - | - | - | - | - | 27763 | 0
| TEC (Tuvalu) | 6278 | - | - | - | 135 | - | 6413 | 2.1
| TPL (Tonga) | 45214 | - | - | - | - | - | 45214 | 0
| UNELCO (Vanuatu) | 53274 | - | - | 5388 | - | 571 | 59233 | 10.1
| YSPSC(Yap,FSM) | 13000 | - | - | - | - | - | 13000 | 0
| Total | 1147150 | 2324251 | 953956 | 11808 | 251 | 17114 | 4454530
| % of Total | 25.8% | 52.2% | 21.4% | 0.3% | 0.01% | 0.7% | 100% | 22.1
Notes: 1. Total is for main grid system only, not entire utility generation. Blank spaces = zero 2. Data as reported by the utilities; for some (e.g. PPUC, TAU) there may be some unreported PV 3. * Excludes CUC power purchases of 74,864 MWh; includes FEA biomass energy purchase. 4. ** ADO/IDO = Automotive Diesel Oil; Industrial Diesel Oil (light petroleum fuels) 5. *** HFO/IDO = Heavy Fuel Oil; Industrial Fuel Oil (heavy petroleum fuels) 6. + RE = Renewable Energy

## Tab 2.7a
content
Table 2.7a: Utility structures, ownership, policies, regulation and coverage
| Utility | Govt ownership | Provides non-electric services? |  | Non-grid or rural supply | Govt / Cabinet appoints board? | Electricity legislation? | External regulation?
|  |  | y or n? | If yes, type |  |  |  | Technical? | Commercial?
| CPUC (Chuuk, FSM) | 100% | yes | water supply | Standalone PV and SHS* | Yes | Yes, CPUC Act 1996 | No | No
| CUC (Saipan) | 100% | Yes | Water waste mamagement | No | no | Public Law 4-47 enacted by Legislature | yes both Commonwealth Public Utility Commission
| EDT (Tahiti) | 99.99% private | no | N/A | A few mini-grids; no obligation to develop more | No but represented by Energy Ministry | No | SEM is technical regulator Tariff set by Concession formula negotiated every 5 years
| EPC (Samoa) | 100% | no | N/A | Grid extension & stand alone PV and PV minigrid (Apolima) | Yes | yes, various Acts 1972-2010 | Regulator created under Electricity Act of 2010 but not yet implemented
| FEA (Fiji) | 100% | no | N/A | Rural grid extensions only | Minister for utilities | yes | Not at present but govt regulation anticipated
| GPA (Guam) | 100% | no | N/A | single grid | General public | Public Law 9-189, May 1968 | Regulated by the Guam Public Utilities Commission and follow nationally recognized standards and policies.
| KUA (Kosrae, FSM) | 100% | no | N/A | single grid; Kosrae is all rural | Governor, legislature | yes, state law Nov 1991 | no | no
| MEC (Majuro, RMI) | 100% | yes | fuel sales | manage rural PV | yes | yes | no | no
| NPC (Niue) | 100% | no | N/A | Rural grid extensions only | no board | no, part of Public Works | no | no, only Cabinet
| NUA ( Nauru) | 100% | yes <1% | water, fuel | N/A | no board | yes, June 2011 | planned | planned
| PPL (PNG) | 100% | no | N/A |  |  | Yes
| PPUC (Palau) | 100% | no | N/A | Standalone PV and diesel systems; Grid connected PV | No | Yes | no | no
| PUB (Kiribati) | 100% | yes | water supply and sewage | standalone PV and SHS | yes | Public Utility Act 1997, revised 1998 |  | Environment regulation 2001
| SIEA ( Solomon Islands) | 100% | no | N/A | Deisel, Hydro, Standalone PV systems & SHS | yes | Electricity Act 2007, State own Enterprises Act 2009 | Yes | no
| TAU ( Cook Islands) | 100% | no | N/A | Diesel and solar - Pukapuka | yes | yes | no | no
| TEC ( Tuvalu) | 100% | no | N/A | Standalone PV, Diesel and SHS | yes | Electricity Act 1991, Public Enterprises Act 2010 | no | yes - National energy Policy
| TPL ( Tonga) | 100% | no | N/A | Standalone PV, Diesel and SHS | yes | Electricity Act 2007 | Yes | Yes
| UNELCO ( Vanuatu) | No: 100% Private | No | N/A | Rural connection within concesson areas; No stand alone | No but one representative from Energy Minister | No National legislation | Yes | Yes, external monitor & control
| YSPC ( Yap, FSM) | 100% | Yes | Water; Waste Management | All of Yap is essentially rural | Yes, represented by state agencies | Yes, Yap State Law 4-4 | No, selfregulating | Yes; state energy policy
Notes: 1. * SHS = Solar Home Systems (low voltage DC photovoltaic systems) 2. N/A = Not Applicable 3. Data not provided by ASPA & KAJUR

## Tab 2.7b & 2.7c
content
Table 2.7b and 2.7c Utility structures, ownership, policies, regulation and coverage
| Utility | Power quality law or regulation? | Service obligation? | Regulation or requirement for: |  |  | National renewable energy goal for electricity ? | Tariff |  | Tax on electricity inputs or supply? |  |  | National utility or specified service areas?
|  |  |  | IPPs/PPAs | FIT** or net metering | DSM |  | Determined by: | Fuel surcharge? | on electricity sold? | on utility equipment? | on fuel used for power?
| CPUC (Chuuk, FSM) | No- patterned on US regulations | no | no | no | Being considered for future | 30% RE by 2020 | Board | no | USD 0.128/gal | 4% tax on all import goods | USD 0.128/gal | Weno and 4 outer islands
| CUC (Saipan) | US standard | no | Yes -Public Law 16-17 also known as CUC Privatization Law | Net Energy Metering Policy (PL 15-87) | no | 40% RE by 2012 | Utiltiy Board | yes | No | yes | Yes | Saipan, Tinian and Rota
| EDT (Tahiti) | LV 10% HV 7-10% freq. 5% | Every paid extension must be connecte | French standards | Yes clear policy & tariffs for PV & wind | No; DSM services are provided | 50% RE by 2020 | Concession agreement | No | Territorial & city taxes + 5% VAT |  | Taxed but varying subsidies to stabilise cost | 20 islands; 90% of population of French Polynesia
| EPC (Samoa) | no | Yes | no | no | no | 20% RE by 2030 | Government | yes | no | no ? | S$0.4/l of IDO + 15% VAT | National; 97% coverage
| FEA (Fiji) | distribution voltage 6%; freq. 2% | no | FEA grid code for IPPs | yes; currently F$0.23/kWh | commercial audits at FEA cost | 90% RE by 2015 | Commerce Commission | not currently | 12.5% VAT paid by consumer | no duty for RE equipment | F$0.18/litre IDO; F$0.10/l HFO | Main Island of Viti Levu, Vanua Levu & Ovalau
| GPA (Guam) | US standard | Yes - On Utility approval | no | net metering | yes | 5% net elctricity sale from RE by 2015 | Guam Public Utilities Commission | yes | no | no | no | Through out Guam
| KUA (Kosrae, FSM) | voltage ±5%; 7.5% industry | no | under consideration | no | no | No; state energy plan being developed | Board of Directors | yes | no | 4% | no | State of Kosrae, FSM
| MEC (Majuro, RMI) | no | planning only | no | no | no | 20% RE by 2020 | Cabinet | no | no | 8% | no | Majuro, Jaluit, Wotje
| NPC (Niue) | NZ but no compliance | Safety only | no | no | Only with donor $ | 100% carbon neutral by 2013 | Govt | no | yes; 12.5% paid by utility | no | no | national, single island
| NUA ( Nauru) | being considered | no | being prepared | no | no | 50% RE by 2015 | Govt | no | no | no | no | national, single island
| PPL (PNG) | AS/NZS 3000:2007 | [7 empty] | 10% GST added to bill
| PPUC (Palau) | Yes | No but PPUC is given a task to electrify the whole of Palau | Yes, within the confines of the law which created the utility. |  |  | 20% RE by 2020 | Utiltiy Board | yes |  | no | USD 0.05/gal | main Island and three other oulying states | Table 2.7c Utility structures, ownership, policies, regulation and coverage
| PUB (Kiribati) | AS/NZS 3000:2007 |  |  |  |  | Reach 70% of population with RE; date ? | Price Ordinance Act 1976, revised 1981 |  |  | no |  | South Tarawa
| SIEA ( Solomon Islands) | AS/NZS 3000:2007 | Community Service Obligation (SCO) Regulation | Yes - technical standard requirements | no | no | 20% RE by 2018 | Govt under the Electricity Tariff Regulation 2005 | Yes |  | yes | SBD$0.22/litre plus 10% GST | Auki, Malu’u, Gizo, Noro, Munda, Kirakira, Lata, Buala, Tulagi and Honiara
| TAU ( Cook Islands) | AS/NZS 3000:2007 | Yes - On Government approval | yes | Net metering | no | 50% RE by 2015; 100% by 2020 | Board | no |  | 100% levy exemptions | Port charges and VAT | Rarotonga
| TEC ( Tuvalu) | AS/NZS 3000:2007 | no | no | no | Being considered | 100% RE by 2020 | Board | yes | 3% for > 50kWh consumption | no | 0.05cent rebate for every litre of fuel purchased | Funafuti and all the outer islands except Niulakita Is
| TPL ( Tonga) | AS/NZS 3000:2007 |  |  |  |  | 50% RE for the the main grid by 2012 | Electricity Commission and TPL | yes |  |  |  | Tongatapu, Vavau, Haapai and Eua
| UNELCO ( Vanuatu) | Yes under concession agreement | Yes, any customer request within concession | No | No | No | No RE goal | Regulated under concession agreement | NO | 12.5% value added tax | No concessions on import duty | 15 vatu/litre | Islands of Efate, Tanna & Malekula
| YSPC ( Yap, FSM) | No but quality is good | Legally no; 100% electrification goal; so yes in practice. | No | Soon net metering to be introduced | No but comm.& households | State goal of 28% with ADB support | Board | d No, built into tariff | No | 4% national import duty; exempt from Yap state tax | 0.05 US$ per US gallon duty; 0.05 US$/USG Yap excise tax | 75% of state: Yap Proper, Ulithi Atoll, Falalop, Woleai
Notes: 1. * IPPs = Independent Power Producers (usually private sector) PPAs= Power Purchase Agreements 2. ** FIT = Feed-in tariff 3. *** DSM = Demand Side Management 4. (?) questionable result
Notes: 1. * IPP = Independent Power Producer; PPA = Power Purchase agreement 2. ** FIT = Feed-in tariff 3. *** DSM = demand side management (for customer energy efficiency services) 4. + RE = Renewable Energy 5. GST = Goods & Services Tax 6. VAT = Value Added Tax 7. No data provided by ASPA and KAJUR

## Tab 2.7a-c
content
Information from Table 2.7a-c is summarised below for the utilities that provided information:
| Ownership | 19 of the 21 utilities that participated in the 2011 benchmarking exercise were 100% government owned in 2010.
| Utility services | Six of 19 utilities that responded provided non-electricity services such as water supply, sewerage, and waste management and/or fuel sales. In some cases, some costs of these services are charged to electricity operations, or not adequately accounted for. This can lead to reported costs (and losses) that should be charged to the water, waste or sewerage operations. Utilities should better allocate costs among services to accurately reflect the actual costs of the services and clearly show subsidies or cross-subsidies where these exist.
| Off-grid supply | Over half of the utilities have some responsibility for off-grid supply away from a main grid, usually stand-alone rural low-voltage DC photovoltaic systems but in some cases small diesel or hydro mini-grid systems. These remote systems often require considerable time and resources, without sufficient compensation to fully cover utility costs. For some utilities, governments have established artificially low users‟ fees for off-grid supply, imposing additional costs on the utility or resulting in poor operations and maintenance of the systems.
| Boards | In general the government appoints most or all members of the utility board of directors but two of the utilities have no formal board.
| Legislation | All but two utilities operate under formal power sector legislation (although some legislation is quite out-dated).
| Regulation | Most of the utilities have no formal system of external regulation (technical or commercial) but commercial regulation exists (e.g. Fiji, PNG, and Vanuatu) or is under development or consideration in several PICTs (e.g. Samoa, Tonga). External regulators in other regions of the world often encourage or require a regular performance benchmarking programme. Most Pacific utilities are the only organisations in the country with technical knowledge of the power sector and are self-regulating technically, but with strong government influence on the level of tariffs.
| Service obligations | Most have no formal public service obligation.
| Quality standards | Many have some form of regulation of power standards (voltage fluctuations and/or frequency) but not all are enforced.
| Private supply regulations | Only three of the 19 utilities have formal regulations for Independent Power Producers (IPPs) and utility Power Purchase Agreements (PPAs) from IPPs (with others under consideration), so some proposed IPP arrangements can be ad hoc and may be difficult to negotiate, limiting the potential for cost-effective independent supply.
| Net metering or feed-in tariffs | Only five of the 19 utilities that responded have either net metering regulations or feed-in tariffs (FITs)8 so it can be difficult for consumers or small businesses to legally provide power to the grid with clear rules, from renewable (or other) energy systems, such as household PV systems being installed or considered in some PICTs (and increasingly common outside of the Pacific).
| Renewable energy goals | Most of the governments have established specific national goals and timetables for electrification through renewable energy. These tend to be very ambitious and many have been developed with little substantive utility input or serious consideration of practicality. They tend to be statements of broad intent.
| Tariff determination | About half of the electricity tariffs are ostensibly established by the board of directors or external independent commissions. In practice, the governments have a very strong influence on  or in some cases effectively decide  tariff levels.
| Charges to Consumers (tariffs) | It can be difficult to compare costs of supply on a consistent basis as some of the utilities pay import duty or tax on fuel and/or equipment, but others do not. Similarly, published tariff schedules do not always clearly indicate all charges to consumers. Some add government taxes and a range of other charges (e.g. insurance) to the bill, but others include these in the tariff schedule. Some tariffs indicate only a „base charge‟ with additional fuel surcharges that often change frequently and can be difficult for consumers to understand or challenge.
| Service coverage | Finally, the systems range from a single distribution voltage grid covering customers on only a single island to those covering many islands and dispersed rural communities with several main grids, a number of smaller isolated grids, and standalone systems. A few have national coverage but others (e.g. in the FSM) only cover specific states.

## Tab 2.8
content
Table 2.8 Utility transmission and distribution voltages (kV)
| Utiltity | Transmission (kV) | Distribution (kV) | Frequency (HZ)
| CUC * (Saipan) | 34.5 | 13.8 | 60
| EDT (Tahiti) | 30; 90 | 11; 14; 20 | 50
| EPC (Samoa) | 22;33 | 6.6; 22 | 50
| FEA (Fiji) | 33;132 | 11 | 50
| GPA (Guam) | 110 & above | 13.8 | 60
| RMI & FSM ** | none | 13.8 | 60
| NPC (Niue), NUA (Nauru), PUB (Kiribati), TAU (Cook Isl.), TEC (Tuvalu), TPL (Tonga) | 33 | 11 | 50
| PPUC (Palau) | 34.5 | 13.8 | 60
| UNELCO (Vanuatu) | None | 5.5 | 50
Notes: 1. * In Rota & Tinian, 13.8 kV distribution only 2. ** RMI = MEC and KAJUR; FSM = PUC, CPUC, KUA & YSPSC

## Table 3.1
content
Table 3.1: Key Benchmark Indicators (2000 and 2010)
| Key Indicators* Used in 2002 report | Explanation or definition from the 2002 report | Average for 2002 | Goals for future as agreed in 2002
Generation
| Load factor | Annual Generation (MWh) * 100 Peak generated load (MW) * Period hours (8,760) | 67% | 50-80%
| Capacity factor | Annual Generation (MWh) * 100 Installed plant capacity (MW) * Period hours (8,760) | 34% | > 40%
| Availability factor | Installed plant capacity (MW) * hours (8,760) - MWh losses * 100 Installed capacity (MW) * Period hours (8,760) | 93% | 80%-90%
| Specific fuel oil consumption (kWh / litre) | Units Generated / Fuel Used | 3.79 | 3-4
| Lube oil consumption (litres / hour) | Lubricants used (volume) Hours of operation | 3.5 | 3.2 - 3.5
| Forced outage | MWh out of service due to forced outages * 100 Installed plant capacity (MW) * Period hours (8,760) | 7.93% | 3-5%
| Planned outage factor | MWh out of service due to planned outages * 100 Installed plant capacity (MW) * Period hours (8,760) | 4.3% | 3%
| O&M cost per /MWh | Total operation and maintenance costs Electricity sent out to grid (MWh) |  | 18
Transmission**
| Reliability | Unplanned outage * 100 / Length of line | Not available
| Transmission Losses | Energy sent out - Energy sent to distribution system Energy sent to distribution system | 8.02% | 5%
Distribution
| Customers/employee | Average total number of customers Average no. of employees in distribution & consumer services | 242 | 240
| Reliability / km | No of unplanned outages * 100 Total length of line
| Transformer utilisation | Total energy sold (MWh) * 100 Distribution transformer capacity (MVA) * 8760 hr | 18.14% | 30%
| Distribution Losses | Electricity sent out - electricity sold Electricity sent out | 12.34% | 5%
| SAIFI (interruptions/customer) | Total number of customer interruptions Average total number of customers | 19 | 10
| SAIDI (hours/customer) | Total customer hours interrupted * 60 Average total number of customers | 592 | 200
| Distribution O&M US$/km *** | Distribution operation and maintenance costs Total circuit kilometres or miles | 2478 | 800
Corporate/Financial
| Operating ratio | Total operating expenses + depreciation Operating revenue | 186% | 0%
| Debt to equity ratio | Long term debt / (Equity + long term debt) | 26.07% | <50%
| Rate of return | Operating income Average net fixed assets in operation | -16.8% | > 0%
| Current ratio | Current assets / Current liabilities | 3:01 | >1:1
| Debtor days | Debtors at year end * 365 / Total revenue | 79 days | < 50 days
Notes: 1. * Slightly edited from 2002 benchmarking summary report. Several indicators slightly renamed or formulas modified for clarity. 2. ** In effect ‘transmission’ refers only to the utilities with high-voltage supply above 33 or 34.5 kV. 3 . ***This was reported to be a questionable result in 2002. 4. + This figure to be discussed at the next CEOs meeting.

## Tab 4.2 & 4.3
content
Table 4.2 Utility demand side management efforts in 2010
| Response from utilities | No of utilities reporting | Comments
| No response | 11 | DSM section of questionnaire left blank
| No DSM staff or N/A | 6 | As above
| Some Full time DSM staff | 4 | Either one or two staff
| Budget for DSM | 5 | Ranges from $0-75,000 *
| Savings made in 2010 | 1 | 1 MWh
Notes: 1. N/A = not applicable 2. * Average = US$35,000
Table 4.3 Composite indicator suggestive of utility technical performance
| Overall Ranking | Utilities | Score (Maximum of 4.0)
| Higher | EDT, FEA, GPA, PPUC, PUB, TPL | 3.0 - 3.8
| Medium | CUC, EPC, PPL, SIEA, TAU, TEC, YSPSC | 2.6 - 2.8
| Lower | CPUC, KUA, MEC, NPC, NUA | 2.2 - 2.5
Notes: 1. For Higher, Medium & Lower ranking, utilities are listed in alphabetical order, not by score 2. Insufficient data for KAJUR and UNELCO so they were not included.

## Tab 5.1
content
Table 5.1 Key indicators compared for 2002 & 2011 Pacific benchmarking reports (2002 report based on 2000 data) (2011 report based on 2010 data)
| Key Indicators |  | 2002 results |  | Future goals | International best practice | 2011results
|  |  | Av | Med | Agreed in 2002) | 2002 report | Av | Med
Generation
| Load factor (%) | ↑ better | 67 | 66 | 50-80 | 50-80 | 64 | 65
| Capacity factor (%) | ↑ better | 34 | 33 | >40 | 35-65 | 32 | 31
| Availability factor (%) | ↑ better | 93 | 97 | 80-90 | 1965-10-01 | 98 | 100
| Specific fuel oil consumption (kWh/ litre) | ↑ better | 3.8 | 3.7 | 4 | >4 | 3.8 | 3.8
| Lube oil consumption (kWh/litre) | ↑better | 3.5 | 2 | 3.2-3.5 | No standard | Not useful; Not calculated
| Forced outage factor (%) | ↓ better | 7.9 | 3.2 | 3-5 | 0 | 0.9 | 0.1
| Planned outage factor (%) | ↓better | 4.3 | 3.9 | 3 | 3 | 2 | ~0(?)
| O&M (USD per MWh) | varies | 58 | 14 | 18 |  | 148 (?) | 71(?)
Transmission
| Transmission losses (%) | ↓ better | 8 | n.a | 5 | 5 | ? Data errors
Distribution
| Customers/employee | ↑ better | 242 | 224 | 240 | 350 | 334 | 297
| Transformer utilisation (%) | ↑ better | 18 | 18 | 30 | 50 | 19 | 21
| Distribution losses (%) | ↓ better | 12(?) | n.a | 5 | 5 | 12? (10 replies)
| SAIFI (interruptions/cust) | ↓better | 19 | 8 | 10 | 0.9 | 8.2 (?) | 3.8(?)
| SAIDI (mins/customer) | ↓better | 592 | 33 | 200 | 47 | 530(?) | 139
| Distribution O&M (USD/km) | Varies | 2478 (?) |  | 800 | 167 | ?
Corporate / financial
| Debt to equity ratio (%) | ↓better | 26 | n.a | <50 | <50 | 15 | 17
| Rate of return on assets (%) | ↑ better | -16.8 |  | >0 | >10 | 9.2(?) | 1(?)
| Current ratio (%) | ↑ better | 3:1 | 1.3 | >1:1 | 1:1 | 2.9:1 | 1:8
| Debtor days (days) | ↓ better | 79 | 51 | <50 days | 30 days | 115 | 56
20 utilities
Notes: 1. n.a. = not available 2. (?) = questionable result 3. See Table 3.1 for definitions of the indicators
:1

## Tab 5.2
content
Table 5.2 Key indicators compared for Pacific and other small utilities
| Indicator | Pacific (Average & Median) |  | CARILEC (Average) | NESIS (Average) |  |  | APPA (Median)
| Data for operational year | 2010 |  | 2008 | 2006 |  |  | 2009
| No. of participating utilities | 21 (but limited data for 2) |  | 21 | 17 groups; 73 islands |  |  | 170
| Utility characteristics | Most small, remote & oil dependent; most 100% govt-owned. Range of 900 -150,000+ customers, with median of 8,300 |  | Most small, remote & oil dependent; much higher GDP/capita than PICs; Govt, private & mixed ownership | EU-linked; much higher GDP/capita than PIC;; Govt, private & mixed ownership. Islands are listed in 3 categories below.(14 of 21 PICTs<100 GWh) |  |  | US public-owned; typically generation < 10% of supply; 82% have < 50,000 customers
| Generation | Average | Median | Median | > 1000 GWh | <1000 GWH | <100 GWh
| Load factor (%) | 64 | 65 | 74.2 |  |  |  | 54.8
| Capacity (utilisation) factor (%) | 32 | 31 | 42.4
| Reserve plant margin (%) | 114 | 91 | 60.5
| Availability factor (%) | 98 | 100 | 82.9
| fuel consumption (kWh/ litre) | 3.8 | 3.8
| Lube oil use (kWh/litre) | 1300 | 970
| Forced outage factor (%) | 0.9 | 0.1
| Planned outage factor (%) | 2 | 0
| O&M (USD per kWh) | 148 | 71
Transmission and Distribution losses*
| System losse (%) | 12.8 | 11.6 | 13 | 9.7 | 6.9 | 9
| T & D technical losses (%) | 5.6 | 5.9 | 6
| Non-technical losses (%) | 7.2 | 5.2 | 3
Distribution
| Customers/employee | 334 | 297 |  |  |  |  | 333
| Unplanned outages/km | (?) | (?)
| Transformer utilisation (%) | 19 | 21
| Distribution losses (%) | 12 ? | ? |  |  |  |  | 3.93
| SAIFI ** (see note 3) | 8.2 | 3.8 | 6.38
| SAIDI** (min/year/employee) | 530 | 139 | 580 | 176 | 77 | 309
| Distribution O&M (US$/km) | (?) | (?) |  |  |  |  | 3738
| Distribution O&M (US$/kWh) | (?) | (?) |  |  |  |  | 0.078
Corporate/financial/misc
| Debt to equity ratio (%) | 15 | 17
| Rate of return on assets (%) | 9.2 | 1 | 6.4
| Current ratio (%) | 2.9:1 | 1.8:1 |  |  |  |  | 2.02
| Debtor days (days) | 115 | 57
| Gen.cost (US$/kWh)*** | (?) | (?) | 0.264 | 0.126 | 0.169 | 0.274
| Tariff (US$/kWh) household + | 0.39 | 0.41 | 0.366 |  |  |  | 0.094
| commercial | 0.47 | 0.44 | 0.387 |  |  |  | 0.092
| Customers/employee (total) | 85 | 74 | 135 | 278 | 167 | 125
| Work incidents/100 employees | (?) | (?) | 3
Notes: 1. *From KEMA supply side loss reports. 2. **PICT data are comparable to the region’s total system losses and presumably wrongly reported 3. SAIFI & SAIDI: Data insufficient for benchmarking & some are inconsistent for CARILEC (and probably PICTs). 4. ***Generation costs for NESIS & APPA include purchased electricity; NESIS costs based on €1.0 = US$1.25 in 2006. 5. +PICTs based on 200 kWh per m for households, 500 kWh per m commercial; CARILEC 100 & 2000 respectively. 6. (?) indicates data may not be sufficiently reliable for meaningful comparisons.

## Table 7.1
content
Table 7.1 Revised Pacific regional benchmarking indicators and goals for CEOs’ consideration
| Key Indicator | Goals for future as agreed by CEOs in 2002 | International Best Practice (2002 report) | Reported Results in 2011 (Median) | Goals for future?
Generation
| Load factor | 50-80% | 65-80% | 65% | 70-75%
| Capacity factor | > 40% | 35-65% | 31% | 60%
| Availability factor | 80%-90% | 10-65% | 100% | Overall: 60%; New plant: >70%
| Reserve Margin |  | 30-60% | 91% | 60%
| Lube oil consumption (litres / hour) | 3.2 - 3.5 | No standard | Not used | Not useful
| Lube oil consumption (kWh/litre) | - | - | 970% | ~1 MW: 500-600; ~4-5 MW: 1000-1300
| Specific fuel consumption medium speed (kWh / litre) | 4 | 4.5 | 3.6-3.8* | >4
| Forced outage | 3-5% | 3% | 0.1% | 3-5%
| Planned outage factor | 3% | 3% | 0.05% | 3-5%
| O&M cost per /MWh | 18 |  | 71 | Report but no goal**
Transmission**
| Transmission Losses | 5% | 5% | n.a | < 10% T&D combined
Delivery system losses
| Technical |  |  | 5.9% | < 5%
| Non-technical |  |  | 5.2% | < 3 %
| Station auxiliary use | None | - | 4.8% | <5
| Customers/distribution employee | 240% | 350 | 297% | 300
| Distribution transformer utilisation | 30% | 50% | 21% | <50%
| Distribution Losses | 5% | 5% | 12%(?) | Combine with T** losses
| SAIFI (interruptions/customer) | 10 | 0.9 | 3.8% | 2017-10-06
| SAIDI (hours/customer) | 200 | 47 | 139% | 100
| Distribution O&M US$/km *** | 800 | 167 | - | Report but no goal**
Corporate/Financial
| Debt to equity ratio | <50% | <50% | 17% | 20-30%
| Rate of return on assets | > 0% | >10% | 1% | 10%
| Current ratio | >1:1 | 1:1 | 1.8 | 2:1 – 3:1
| Debtor days | < 50 days | 30 days | 57 | <30 days
| Customers/total employees | None | - | 74 | >100 (?)
Notes: 1. * Median differs according to source (questionnaires or KEMA) 2. ** T= Transmission losses 3. *** Or possibly goal using constant $. The old indicators not mentioned in this table remain unchanged but CEOs should consider them as well 4. (?) questionable result

## Appendix 11
content
|  |  | A.3 | A.4 | A.4 | A.4 | A6
| Utility |  | worked days lost | Injury duration rate | injury frequency rate (per million hours) | Training expense | Energy sold
|  |  | % | % |  | % of payroll | GWH
| ASPA | A Samoa | no data | no data | no data | no data | 141.8698
| CPUC | Chuuck | no data | no data | no data | no data | 6.417
| CUC | Saipan | 1.8592 | 1.5717 | 171.8965 | 0.12084 | 271.8399
| EDT | Tahiti | 0.0059438 | 4.7619 | 15.6261 | 1.7666 | 636.2
| EPC | EPC | 0.078015 |  |  |  | 91.7
| FEA | Fiji | 12.0123 | 3.2675 | 4.483 | 2.804 | 754.855
| GPA | Guam | 5.5957e-05 | 7.3864 | 5.6818 | 2.3435 | 1637.6
| KAJUR | Ebeye |  |  |  |  | 12.76
| KUA | Kosrae | 2.1414 | 0 |  | 15.7105 | 5.5114
| MEC | Majuro | no data | no data | no data | no data
| NPC | Niue | 0.78544 | 34.7826 | 24.9875 | 59.2885 | 2.7
| NUA | Nauru | 0.20704 | 7.1429 | 5988.024 | 7.6321 | 13.656
| PPL | PNG | no data | no data | no data | no data | 757
| PPUC | Palau | no data | no data | no data | 3.9564 | 68
| PUB | Kilibati | no data | no data | no data | no data | 20.58
| SIEA | Solomon | no data | no data | no data | no data | 57.2
| TAU | Cooks | 0.052679 | 31.3725 | 1.7609 | 7.895% | 24.8481
| TEC | Tuvalu | 0.080321 | 0 | 0 | 2.4419 | 5.4066
| TPL | Tonga | 0.99174 | 9.0909 | 6000.6001 | 5.9653 | 42.625
| UNELCO | Vanuatu | 3.0682 | 1 | 3.85 | 0 | 55.5
| YSPSC | Yap | 2.1414 | 0 |  | 15.7105 | 11
|  | Average | 1.8018 | 8.3647 | 1221.691 | 9.063
|  | Median | 0.78544 | 4.0147 | 10.6539 | 2.804
|  | Number | 13 | 12 | 10 | 13
| Utility | Generation: | Transmission | Distribution | Other/misc | Total | Generation | Transmission | Distribution | Other/misc | Total
| A | 14648957 |  | 2899643 | 0 | 17548600 | 14648957 |  | 2899643 |  | 17548600
| B | n.a. | 0 |  | 884330 | 884330 |  | - | - | 884330 | 884330
| W | 20151214 | - | 7851153 | - | 28002367 | 20151214 | - | 7851153 | - | 28002367
| S | 12614575209 | 996423125 | 3627480476 | 2353177114 | 19591655924
| E | 53669462 | - | 13695475 | 17413744 | 84778681 | 21467785 | - | 5478190 | 6965498 | 33911472
| G | 5728315 | 1557215 | 9077699 | - | 16363229 | 3014903 | 819587 | 4777736 | - | 8612226
| T | 36864077 | 12803737 | 16036421 | 62909741 | 128613976 | 36864077 | 12803737 | 16036421 | 62909741 | 128613976
I
| H | 2097890 | - | 428227 | 178818 | 2704935 | 2097890 | - | 428227 | 178818 | 2704935
| X |  |  |  |  | - | - | - | - | - | -
| C | 55000 |  | 30000 | 20000 | 105000 | 45082 | - | 24590 | 16393 | 86066
| U | 2458137 | - | 749456 | 233297 | 3440890 | 1293756 | - | 394451 | 122788 | 1810995
| P |  |  |  |  | - | - | - | - | - | -
| J | 20382475 | 1349320 | - | - | 21731795 | 20382475 | 1349320 | - | - | 21731795
| O | 22958437 | - | 3462044 | - | 26420481 | 12083388 | - | 1822128 | - | 13905516
| L | 218010790 | - | 8048660 | 28594000 | 254653450 | 26914912 | - | 993662 | 3530123 | 31438698
| M | 2959559 | 0 | 2444378 | 1840841 | 7244778 | 1973039 | - | 1629586 | 1227227 | 4829852
| V | 1523270 | 0 | 0 | 167515 | 1690785 | 801721 | - | - | 88166 | 889887
| N | 5921225 | 0 | 10159759 | 4838187 | 20919171 | 2960613 | - | 5079880 | 2419094 | 10459586
Q
R
| Ave | 868133601 | 84344450 | 284015664 | 176089420 | 1261509277 | 11495534 | 1069475 | 2822386 | 5416780 | 19605388
| Median | 14648957 | - | 3462044 | 206058 | 16955915 | 2987758 | - | 993662 | 105477 | 8612226
| No | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Notes: 1. From consolidated spread sheet of 7 November 2011 (linked to individual submissions) prepared by P Perelini
|  | B.3 | B.3 | B.3 | B.4 | B.5 | B.6 | B.6 | B.7 | B.8 | from Perelini | B.9 | B.9 | B.10 | B.12 | B.12
| Utility | Load factor utility | Load factor utility+IPP | Power factor | Capacity factor | Reserve Plant Margin | Equip Avail Factor utility | Equip Avail Factor utility + IPP | Labour productivity | Fuel consumption | lube oil consumption | Forced outage | Planned outage | Energy to grid (incl IPPs) | Generation O&M local | Generation O&M
|  | (%) | (%) |  | % | % | (%) | (%) | GWh/generation employee | kWh/litre | kWh/litre | % | % | GWh | $/MWh | US$/MWh
| ASPA | 73.24 | 73.24 | 0.8 | 38.43 | 91 | 99 | 100 | 1.67 | 3.9 | 1025 | 0.04 |  | 156 | 210 | 210
| CPUC | 31.92 | 32 | 0.85 | 31.92 | 0 | 100 | 100 | 0.54 | 3.13 | no | data | - | 0 | 9.23 | –
| CUC | 53.01 | 72 | 0.95 | 29.56 | 102 | 94 | 95 | 2.21 | 3.81 | 386 | 0.01 | 3% | 317 | 71 | 71
| EDT | 61.85 | 61.97 | 0.9 | 30.3 | 104 | 83.2 | 83.2 | 3.64 | 4.62 | 986 | 7.7 | 8.49 | 550 | 18312 | 193
| EPC | 60.53 | 60.53 | 0.8 | 37.39 | 62 | 99 | 99 | 0.95 | 4.08 | 2075 | 0.48 | 0.39 | 110 | 482 | 193
| FEA | 63.92 | 65.25 | 0.85 | 46.75 | 50 | 98 | 99 | 10.09 | 4 | 2487 | 0.07 | 0.97 | 789 | 7 | 4
| GPA | 78.15 | 78.15 | 0.85 | 45.77 | 103 | 100 | 100 | 20.63 |  |  | 3.5 | 6.55 | 1758 | 20 | 20
| KAJUR | 73.59 | 73.59 | 0.8 | 42.61 | 73 | 100 | 100 | 0.75 | 3.98 |  | 0 | 0
| KUA | 68.08 | 68.08 | 0.93 | 15.13 | 350 | 100 | 100 | 0.94 | 3.8 | 3782 | 0.03 | 0.01 | 6 | 320 | 320
| MEC | 75.6 | 75.6 | 0.9 | 25.65 | 195 | 100 | 100 | 0.92 | 3.68 | 535 | ? | ? | 59 | - | -
| NPC | 63.68 | 63.68 | 0.7 | 16.68 | 282 | 100 | 100 | 0.38 | 3.65 | 1227 | 0.01 | 0.004 | 3.1 | 17.93 | 14.69
| NUA | 77.88 | 77.88 | 0.99 | 32.13 | 142 | 100 | 100 | 0.68 | 3.27 | 881 | 0.91 | 0.3 | 22 | 109 | 57
| PPL | 40.74 | 59.56 | 0.8 | 36.72 | 62 | 86 | 99 | 1.23 | 3.3 | 605 | 0.32 | 0.21 | 484 | 0.05 | 0.02
| PPUC | 60.02 | 60.02 |  | 32.59 | 84 | 100 | 100 | 1.18 |  | 526 | - |  | 79 | 245 | 245
| PUB | 55.02 | 55.02 | 0.96 | 45.33 | 21 | 100 | 100 | 0.49 | 3.82 | 2016 | 2.69 | 0 | 21 | 1061 | 558
| SIEA | 69.68 | 69.83 | 0.85 | 31.93 | 20 | 100 | 100 | 1.34 | 3.81 | 955 | ? | ? | 8 | 2607 | 322
| TAU | 65.02 | 65.02 | 0.95 | 30.59 | 13 |  |  | 1.32 | 3.81 | 363 | 0.397 | 14.5 | 27 | 107 | 71
| TEC | 71.91 | 131.15 | 0.8 | 18.68 | 285 |  |  | 0.16 | 3.94 | 2863 | 0.02 | 0.02 | 6 | 349 | 349
| TPL | 67.06 | 67.06 | 0.99 | 40.71 | 65 |  |  | 3.35 | 4.08 | 909 | 0.18 | 0 | 44 | 51 | 26
| UNELCO | 59.84 | 59.84 |  | 28.65 | 109 | 72.72 | 99.13 | 2.82 | 3.94 | 680 | 0.01 |  | 57
| YSPSC | 64.52 | 64.52 | 0.9 | 22.49 | 187 | 2 | 98 | 1.86 | 3.74 | 1140 | 0.17 | 0.06 | 12 | 161 | 161
| Average | 63.58 | 63.38 | 0.87 | 32.38 | 114.26 | 90.8 | 98.43 | 2.72 | 3.81 | 1302.23 | 0.87 | 1.97 | 225.94 | 1340.64 | 148.18
| Median | 64.52 | 65.02 | 0.85 | 31.93 | 90.56 | 100 | 100 | 1.23 | 3.81 | 970.1 | 0.07 | 0.05 | 50.64 | 135.28 | 71.13
| Number | 21 | 21 | 19 | 21 | 21 | 18 | 18 | 21 | 19 | 18 | 19 | 16 | 20 | 18 | 19
|  | C.1 | C.2 | C.3 | C.3 | C.3 | C.4 | C.4 | C.4 | C.4
|  | Reliability Outages/100km | GWh / employee | losses % | transformers MVA | circuit km | O&M cost local $/km | O&M cost local $/MWh | O&M cost US $/km | O&M cost US $/MWh |  | General notes regarding Appendix 11: 1. Some average and median values in this annex may differ from some of those in the text of the report because some outlying values were ignored in calculating indicators. The text accompanying Figures 4.1.1 - 4.6.3 of the report identifies any data not used. 2. Data used to compare 2000 and 2010 utility operations is not included in this Appendix but are available electronically from the PPA as part of the Final Report Performance Benchmarking October 2002 (dated 8 October 2002). 3. Data used for 2010 household & commercial costs per kWh for consumers (Figure 4.5.2) is not legible when translated from Excel to Word but the file is available from the PPA. The filename is “PIC electricity tariffs 2010-11 (PJ rev 7Jul11).xlsx”
| FEA | 17 | 25 | ? | 661 | 388 | 4013 | 2 | 2112 | 1
| GPA | 87 | 39 | 34 | 1994 | 279 | 45839 | 7 | 45839 | 7
| PPL | 314 | 2 | 2 | 529 | 128 | 357 | 0 | 132 | 0
| PPUC | 0 | 3 | 11 | 40 | 76 | 17754 | 16 | 17754 | 16
| Average | 104 | 17 | 16 | 806 | 218 | 16991 | 6 | 16460 | 6
| Median | 52 | 14 | 11 | 595 | 204 | 10884 | 4 | 9933 | 4
| Number | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 4 | 4
|  | D.2 | D.2 | D.2 | D.2 | D.2 |  | D.3 | D.3 | D.4 | D.4 | D.4 | D.4
|  | Distribution Reliability Outages/100km | Customers / Employee | Transformer Utilisation % | Total T&D Losses % | Distribution losses % | Dist loss with error % | SAIFI interruptions/customer | SAIDI min/cust/year | Distribution O&M cost local $/km | Distribution O&M cost local $/MWH sold | Distribution O&M cost US $/km | Distribution O&M cost US $/MWH sold
| ASPA | 15 | 297 | 25 | 9 | 9 |  | 5 | 139
| CPUC | ? | 126 | 9 | 31 | 31 |  | ? | ? |  |  | 0 | 0
| CUC | 19 | 292 | 22 | 14 | 14 |  |  |  | 17331 | 29 | 17331 | 29
| EDT | 7 | 321 | 16 | 7 | 4 |  | 4 | 138 | 1891283 | 7068
| EPC | 28 | 300 | 25 | 21 |  | (79) | 18 | 885 | 26 | 0 | 14 | 0
| FEA | 26 | 436 | 17 | 4 | 4 |  | 21 | 1008 | - | - | - | -
| GPA | 105 | 763 | 21 | 7 |  | (27) | 13 | 15,900ignored | 26289 | 9793 | 26289 | 9793
KAJUR
| KUA | 29 | 168 | 7 | 15 |  |  | 4 | 3736 | 3736 | 30505 | 2491 | 20337
MEC
| NPC | 13 | 218 | 10 | 12 | 12 |  | 11 | 414 | 375 | 11111 | 307 | 9107
| NUA | 89 | 272 | 39 | 38 | 13 |  | 0.82 | 55 | 13879 | 55 | 14850 | 59
| PPL | 6 | 423 |  | 22 | 20 |  | 0.02 |  | 48.12 | 31.78 | 25.33 | 16.73
| PPUC | 53 | 215 | 24 | 15 | 4 |  | 0.01 | 0.46 | 17754 | 16 | 17754 | 16
| PUB |  | 538 | 24 |  |  |  | ? | 0.35 | 21503 | 168 | 14336 | 112
| SIEA | 232 | 500 | 22 | 30 |  | (70) | 50 | 323
| TAU | 15 | 375 | 18 | 9 | 9 |  | 1.23 | 48.9 | 8466 | 98373 | 4233 | 49186
| TEC | 184 | 475 | 0 | 49 |  |  | 0 | 2 | 20962 | 61259
| TPL | 33 | 237 |  | 15 |  |  | 0.32 | 0 | 51677 | –
| UNELCO | 4 | 276 | 25 |  |  |  | - | 382
| YSPSC | 10 | 115 | 14 | 54 |  | 54 | 3.82 | 814
| Average | 50.98 | 334.09 | 18.76 | 20.72 | 11.99 |  | 8.2 | 530 | 148095 | 15601
| Median | 26.22 | 297.1 | 20.88 | 15.11 | 10.64 |  | 3.8 | 139 | 15605 | 112
| No | 17 | 19 | 17 | 17 | 10 | 4 | 16 | 15 | 14 | 14 | 12 | 12
| utility | E.1 | E.2 | E.3. | E.4 | E.6 | E.7 | E.7 | E.7 | E.7 | E.7 | E.7 | E.7 | E.7
|  | Return on total operating assets | Debt Equity Ratio | Return on Equity | Current Ratio | Debtor Days | Ave price of electricity sold | Ave cost of electricity sold | Profit per MWH sold or delivered | Ave cost of electricity generated | Ave price of electricity sold | Ave cost of electricity sold | Profit per MWH sold or delivered | Ave cost of electricity generated
|  | % | % | % | Assets/liabilities | days | local $/MWh | local $/MWh | local $/MWh | local $/MWh | US$ / MWh | US$ / MWh | US$ / MWh | US$ / MWh
| A | 5.38 | 1.86 | 6.2 | 2.55 | 22 | 316.71 | 124 | 193 | 92 | 317 | 124 | 193
| B | -60.49 |  |  | 0.1 |  | 528 | 709 | -180.82 |  | 528 | 709 | -181 | –
| C | 17.75 | 0 |  | 0.69 | 71 | 103.01 | 283.36 | 180.35 | 63.59 | 598 | 283 | 180 | 63.59
| E | 0.97 | 17.26 | 1.3 | 3.14 | 24 | 32043 | 30795 | 1248 | 18312 | 396 | 12317.92 | 499.34 | 7324.97
| G | 2.71 | 31.18 | 0.61 | 1.73 | 35 | 989.31 | 949.41 | 39.9 | 0 | 125 | 500 | 21 | 0
| H | -11.09 | 1.24 | -12.64 | 2.59 | 114 | 237.93 | - | 237.93 | - | 380 | - | 238 | –
| I | [5 empty] | 223.7 | 78.54 | 145.17 | 19.8 |  | 79 | 145 | 19.8
| J | -4.04 | 23.94 | -7.04 | 2.53 | 64 |  |  |  |  | 350
| L | -9.1 | 25.5 |  | 4.69 | 57 | 380.28 | 490.79 | -110.51 | 319.78 | 1003 | 402 | -91 | 262.12
| M | 8.22 | 3.73 | 6.73 | 7.19 | 23 |  |  |  |  | 489 | - | - | -
| N | 7.56 | 16.96 | 9.19 | 0.93 | 12 | 729 | 39 | 690 | 17927 | 430 | 14 | 256 | 6640
| O | -1.72 |  |  | 1.32 | 116 | 137.83 | 251.97 | -114.14 | 109.19 | 244 | 252 | -114 | 109.19
| P | 8.87 | 36.45 | 5.66 | 1.81 | 53 | 711.47 | 575.59 | 135.88 | 54.54 | 264 | 303 | 72 | 28.7
| Q | 245.6 | 0.27 | 10.84 | 1.67 | 56 | 350.04 | 323.87 | 26.17 | 245.35 | 531 | 40 | 3 | 30.29
| R | -11.09 | 1.24 | -12.64 | 2.59 | 114 | 464.44 | 1283.79 | -819.35 | 1060.88 | 380 | 856 | -546 | 707.25
| S | 2.63 | 18.47 | 9.27 | 1.43 | 117 | 8126.37 | 4451.98 | 3674.39 | 2607.07 | 372 | 2343 | 1934 | 1372.14
| T | 2.1 | 31.02 | -5.35 | 4.66 | 742 | 734.14 | 291.56 | 442.58 | 106.6 | 224 | 146 | 221 | 53.3
| U | 7.17 | 7.57 | 11.27 | 12.82 |  | 722 | 564 | 158 | 349 | 73
| V | 0.42 | 21 | -2.48 | 0.73 | 56 | 0.86 | - |  |  | 380
| W | -1.47 | 22.67 |  | 1.45 | 276 | 48715 | 43354 | 5361 | 23231 |  | 503 | 62.25 | 269.75
| X | ? | ? | ? | ? | ? | 380.28 | 490.79 | -110.51 | 161.38 |  | 490.79 | -110.51 | 161.38
| Average | 9.2 | 15 | 1 | 2.9 | 114.6 | 5047 | 4477 | 622 | 3804 | 394
| Median | 1 | 17 | 3 | 1.8 | 56.9 | 464 | 491 | 151 | 161 | 380
| No | 19 | 17 | 14 | 19 | 17 | 19 | 19 | 18 | 17 | 18 | 18 | 18 | 17
| Utility | Station losses | Unmetered | Tech | Non-Tech | Tech + Non-Tech | Total | Own use if metered | Other* |  |  | Utility | Year | SFC* kWh / USG) | SFC kWh/l
| CPUC | 3.8% |  | 7.7% | 16.1% | 23.8% | 27.6% |  | 5.72% | lights,water&sewerage |  | CPUC | 2009 | 13.4 | 3.54
| CUC | 4.7% |  | 4.4% | 10.7% | 15.1% | 19.8% |  | 0.98% | lights,water&sewerage |  | CUC | 2009 | 13.6 | 3.59
| FEA | 1.1% | 0.01% | 7.5% | 0.8% | 8.3% | 9.4% | 0.02% |  |  |  | GPA | 2009 | 14.52 | 3.84
| GPA | 5.4% |  | 6.4% | 0.5% | 6.9% | 12.2% |  | 0.17% | ownbuildinguse |  | KAJUR | 2009 | n/a | n/a
| KAJUR | 4.2% |  | 2.8% | 12.6% | 15.4% | 19.5% |  | 3% | lights,water&sewerage |  | KUA | 2009 | 13.75 | 3.63
| KUA | 5% |  | 5.9% | 3.3% | 9.2% | 14.2% |  | 2.58% | streetlights |  | MEC | 2009 | 15.18 | 4.01
| MEC | 8.5% |  | 6.4% | 11.4% | 17.8% | 26.2% |  | 0.67% | streetlighting |  | NPC | 2010 | 15.79 | 4.2
| NPC | 5.2% |  | 4.7% | 0% | 4.7% | 9.9% |  | 1.94% | streetlighting |  | NUA | 2010 | 12.03 | 3.2
| NUA | 2.3% |  | 4.4% | 15.8% | 20.1% | 22.4% | n/a |  |  |  | PPUC | 2009 | 13.22 | 3.49
| PPUC | 6.5% |  | 7.6% | 4.3% | 11.8% | 18.4% |  | 0.76% | streetlighting |  | PUC | 2009 | 13.62 | 3.6
| PUB | 4.8% | 2.76% | 5.9% | 5.2% | 11.1% | 18.7% | 1.93% |  |  |  | TAU | 2010 | 14.28 | 3.8
| PUC | 5.1% |  | 5.9% | 5.7% | 11.6% | 16.7% |  | 1.94% | lights,water&sewerage |  | YSPSC | 2009 | 13.93 | 3.68
| SIEA | 2.9% |  | 7.3% | 15.6% | 22.9% | 25.8% | n/a |  |  |  | Average |  | 13.94 | 3.69
| TAU | 2% | 1% | 4.4% | 3% | 7.4% | 10.3% | n/a |  |  |  | Median |  | 13.75 | 3.63
| TEC | 8.6% | 1% | 3.6% | 3.5% | 7.2% | 16.8% | 2.51% |  |  |  | Notes: 1. *SFC = specific fuel consumption
| TPL | 3% | 1% | 3.8% | 9.7% | 13.5% | 17.5% | n/a
| YSPSC | 7.4% |  | 6.4% | 4% | 10.4% | 17.9% |  | 7.59% | lights,water&sewerage
| Count | 17 |  | 17 | 17 | 17 | 17 |  | 10
| Average | 4.7% |  | 5.6% | 7.2% | 12.8% | 17.8% |  | 2.5%
| Median | 4.8% |  | 5.9% | 5.2% | 11.6% | 17.9% |  | 1.9%
Notes: 1. * ‘Other’ Includes unmetered deliveries for street lights, water, sewerage facilities, etc. except for Fiji, which is metered 2. Data for north Pacific (US standards) are from KEMA studies on Quantification of Energy Efficiency in the Utilities of the U.S. Affiliate States (excluding US Virgin Islands. 2010 3. Data for NPC, NUA & TAU are from KEMA studies (or drafts) on Quantification of Energy Efficiency in the Utilities of the South Pacific, 2011. 4. Others are draft KEMA spreadsheet summaries prepared by I Toimoana with PJ 13 July; Updated/expanded PJ 18 November 2011.
| Utility | Specific Fuel Consumption |  |  | Capacity factor |  |  | System Losses |  |  |  | Labour Productivity |  |  | Composite of four indicators | Composite Indicator Sorted from low to high value
|  | Kwh/litre | Adjust | Source | Equip use | Adjust | Source | Losses (%) | 1.0 minus losses | Adjust | Source | Customers/ |  | Source
[12 empty] | Employee | Adjust
| ASPA | 3.9 | 0.84 | Q2 | 38.43 | 0.82 | Q2 | [7 empty] | n.a. |  |  | Utility
| CPUC | 3.13 | 0.68 | Q2 | 31.92 | 0.68 | Q2 | 0.238 | 0.762 | 0.8 | K | 29.18 | 0.13 | Q2 | 2.29 |  | 2.22 | KUA
| CUC | 3.81 | 0.82 | Q2 | 29.56 | 0.63 | Q2 | 0.151 | 0.849 | 0.89 | K | 64.05 | 0.28 | Q2 | 2.63 |  | 2.27 | NPC
| EDT | 4.62 | 1 | Q2 | 30.3 | 0.65 | Q2 | 0.07 | 0.93 | 0.98 | Q2 | 166.41 | 0.74 | Q2 | 3.36 | L | 2.29 | CPUC
| EPC | 4.08 | 0.88 | Q2 | 37.39 | 0.8 | Q2 | 0.21 | 0.79 | 0.83 | Q2 | 63.39 | 0.28 | Q2 | 2.79 |  | 2.39 | MEC
| FEA | 4 | 0.87 | Q2 | 46.75 | 1 | Q2 | 0.083 | 0.917 | 0.96 | K | 224.98 | 1 | Q2 | 3.83 |  | 2.52 | NUA
| GPA | 3.84 | 0.83 | K | 45.77 | 0.98 | Q2 | 0.069 | 0.931 | 0.98 | K | 90.68 | 0.4 | Q2 | 3.19 |  | 2.6 | YSPSC
| KAJUR | 3.98 | 0.86 | Q2 | 42.61 | 0.91 | Q2 | 0.154 | 0.847 | 0.89 | K | 80.22 | 0.36 | Q2 | n.a. |  | 2.62 | TAU
| KUA | 3.8 | 0.82 | Q2 | 15.13 | 0.32 | Q2 | 0.092 | 0.908 | 0.95 | K | 26.84 | 0.12 | Q2 | 2.22 |  | 2.63 | CUC
| MEC | 3.68 | 0.8 | Q2 | 25.65 | 0.55 | Q2 | 0.178 | 0.822 | 0.86 | K | 41.43 | 0.18 | Q2 | 2.39 | M | 2.73 | PPL
| NPC | 3.65 | 0.79 | Q2 | 16.68 | 0.36 | Q2 | 0.047 | 0.953 | 1 | K | 27.4 | 0.12 | Q2 | 2.27 |  | 2.75 | SIEA
| NUA | 3.27 | 0.71 | Q2 | 32.13 | 0.69 | Q2 | 0.201 | 0.799 | 0.84 | K | 64.57 | 0.29 | Q2 | 2.52 |  | 2.79 | EPC
| PPL | 3.3 | 0.72 | Q2 | 36.72 | 0.79 | Q2 | 0.22 | 0.78 | 0.82 | Q2 | 91.67 | 0.41 | Q2 | 2.73 |  | 2.83 | TEC
| PPUC | 3.49 | 0.76 | K | 32.59 | 0.7 | Q2 | 0.118 | 0.882 | 0.93 | K | 146.26 | 0.65 | Q2 | 3.03 |  | 3.03 | PPUC
| PUB | 3.82 | 0.83 | Q2 | 45.33 | 0.97 | Q2 | 0.111 | 0.889 | 0.93 | K | 67.75 | 0.3 | Q2 | 3.03 |  | 3.03 | PUB
| SIEA | 3.81 | 0.82 | Q2 | 31.93 | 0.68 | Q2 | 0.229 | 0.771 | 0.81 | K | 97.2 | 0.43 | Q2 | 2.75 | H | 3.1 | TPL
| TAU | 3.81 | 0.82 | Q2 | 30.59 | 0.65 | Q2 | 0.074 | 0.926 | 0.97 | K | 37.46 | 0.17 | Q2 | 2.62 |  | 3.19 | GPA
| TEC | 3.94 | 0.85 | Q2 | 18.68 | 0.4 | Q2 | 0.072 | 0.928 | 0.97 | K | 134.62 | 0.6 | Q2 | 2.83 |  | 3.36 | EDT
| TPL | 4.08 | 0.88 | Q2 | 40.71 | 0.87 | Q2 | 0.135 | 0.865 | 0.91 | K | 99.73 | 0.44 | Q2 | 3.1 |  | 3.83 | FEA
| UNELCO | 3.94 | 0.85 | Q2 | 28.65 | 0.61 | Q2 | [7 empty] | n.a. |  | 2.8 | Ave
| YSPSC | 3.74 | 0.81 | Q2 | 22.49 | 0.48 | Q2 | 0.104 | 0.896 | 0.94 | K | 82.6 | 0.37 | Q2 | 2.6 |  | 2.75 | Median
Sources: 1. Q2 = questionnaire section 2 from utilities 2. K = KEMA study system delivery losses 3. 'Adjusted' sets best value at 1.0 4. PJ 22 Nov 2011 5. Composite uses equal weighting for each of the three measures 6. Insufficient info for ASAP & UNELCO 7. KAJUR ignored due to data errors.
= best value for the indicator